"FULLYAUTOMATED BURNER MANAGEMENT SYSTEM USING PLC"

FACT (THE FERTILIZERS AND CHEMICALS TRAVANCORE LIMITED) was set up in 1944 on the banks of river Periyar at Udyogamandal, Ernakulam. In decades that followed, multistage expansion programming was undertaken bringing in the latest technology of the days, which were quickly mastered and I successfully implemented.

In 1962, FACT came under the government of India. A second fertilizers production unit called Cochin Division (CD) at Ambalamughal and two Engineering divisions FACT Engineering and Design Organization (FEDO) and FACT Engineering Works (FEW) were established. FACT; a government of India enterprise has business interests in manufacturing and fabrication of equipments.

The company has also interests in fields like Petrochemical, Hydro metallurgy, Chemical and Pharmaceuticals etc. Products like Factmfos, Urea gained wide popularity. Next hosting point came with setting up of international standards and is mainly used in production of Nylon. FACT'S next endeavor was 900 TDP ammonia complex, which was set up in Udyogamandal Division (UD) with Japanese collaboration. Now despite a few financial problems, FACT is still growing.

FACT has capital employed of Rs 650 crores and its turnover around Rs 1210.04 crores. FACT has three manufacturing divisions, two at Udyogamandal, Eloor, one at Ambalamedu near to Cochin Refineries. The overall production is in the range of 2.85 lakh tonnes of nitrogen, 1.5 lakh tonnes of Phosphate and 50000 tonnes of Caprolactum. It has wide range of fertilizers from straight fertilizers like Ammonium Sulphate and Urea to Complex fertilizers. It has successfully branched out into the field

| of Chemicals and Fertilizer Technology Engineering and Design capabilities, R&D and

I Fabrication Engineering Services.

POWER DISTRIBUTION IN FACT

FACT Udyogamandal is getting power supply through two 110KV feeders, from the 220KV substation, Kalamassery. Normally one feeder will meet the full demand of the Udyogamandal complex and the other feeder will always be spare, kept isolated in FACT 110KV yard.

Two transformers 1&2 of AEI England make of 15MVA Capacities and other two 3&4 of TELK make of 12.5/20MVA rating. All the four transformers step down the 110K.V voltage to 11KV. The 11KV secondaries of the 1&2 transformers feed JYOTHY Panel and secondaries of 3&4 transformers feed ALIND Panel. Transformers 1&2 are provided with off-load tap changing system, where as 3&4 are provided with on-load tap changing system. All the transformers can be isolated on load at 110KV side by outdoor 110KV SF6 circuit breakers. For the improvement of system power factor two capacitor banks of 1940KVAR and 970KVAR capacities are provided in the 110KV substation. One 970KVAR capacitor is connected at 11KV substation and one 500KVAR bank at S02 acid substation.

There are two outdoor transformers of 5MVA capacity in the 110KV substation, of TELK make which step down 11 KV to 3.3KV to feed NGEF/TMG, 3.3KV panel in the substation. 11KV outgoing feeders from the Jyothy Panel feed the primary sides of six 5MVA transformers in the intermediate 11KV substation.

Demand for the total Udyogamandal complex including Petrochemical division and new 900TPD Ammonia plant is met through separate duplicate 11KV feeders from the Alind Panel. The station low tension demand of the 110KV substation is met by one 750KVA indoor station transformer. The 110KV control panel facilitates remote control of 110KV breakers, the necessary metering and all the

protective relays. TOD meter installed in the 110KV control panel measures various parameters for both recording and billing purpose.

Power is received at the 11OKV substation in FACT Udyogamandal division and distributed to various plants in Udyogamandal division, apart from sending power to FACT Petrochemical division and new Ammonia plant. Besides the KSEB supply, power is generated in the complex by two Turbogenerator units. They are of 6MW capacity in Ammonia plant and 16MW capacity in Petrochemical division. Power can be received and sent from the 11 OKV substation through interconnecting feeders.

tp

-B-

T*^""    ||m"^)^  ,t

Is

H   H

V v

A t

Li

Fig:Power Distribution in FACT

A A" ° i

h ll

The present average energy demand of Udyogamandal division is about 2.85 Lakh units per day with a maximum contract demand of 16MVA.

Running load of various plants in FACT Udyogamandal division is;

| DCDA acid plant | - 1.5MW |
| --- | --- |
| S02 Oleum plant | - 1.2MW |
| Ammophos 300 TPD plant | - 0.63MW |
| Ammophos 150 TPD plant | - 0.48MW |
| Phosphoric acid plant | - 0.83MW |
| Ammonium Sulphate plant | - 1.10MW |
| Filter Bed | - 0.83MW |
| Township and Miscellaneous | - 1.04MW |

SYNOPSIS

.

This project titled "FULLY AUTOMATED BURNER MANAGEMENT SYSTEM USING PLC" is almost entirely centered on the boiler plant |t Ammonia complex of "THE FERTILIZERS AND AGRO-CHEMICALS Ltd, T.RAVANCORE (FACT) unit located at Udyogamandal, Kalamasserry, Ernakulam, Kerala. The plant is equipped with most modern electronic system and hence our exposure to them provide truly beneficial. We begin our work with the study of boilers |hd boiler controls implemented at the plant making use of PLC programmers and. Literatures.

The project aims at different objectives such as automation of plant and energy saving by continuous operation by PLC control, reduction of capital cost and time lost. A programmable logic controller is proposed to be incorporated for the Automation part of project. PLCs have short period of time played a major role in the (evolution of automation both in discrete and process application in industrial control. iPLCs are being used extensively in control system now, where electromechanical relays were in use formerly. The introduction of PLC will make the system more flexible, easy up-gradable and maintenance-friendly.

The project deals with burner management system using ^PLC in boiler process which supervises the control of the fuel burning equipment and :provides all monitoring facility for safe and smooth startup and shut down of boiler.

OBJECTIVES OF PROJECT

Complete automation of burner operations by controlling fuel and steam inputs to the burners.

To meet safety requirements of boiler process control systems.

To provide reliable and efficient operation of system by modifying

interlocks/protection using PLC.

To reduce initial cost & maintenance cost by reducing hardware circuits with relay.

PLCs are programmable according to the requirement.

Application of PLCs ensures continuous operation and there by we can

avoid increased rate of Energy consumption due to frequent starting &

tripping.

PLC ensures the proper burning of fuel in the boiler.

CAPTIVE POWER PLANT

■

•   INTRODUCTION

Captive Power Plant (CPP) is the power generating unit of Replacement Ammonia Plant (RAP). Main objective of CPP is to provide steady and continuous power. In CPP, steam is produced and using this steam Six Megawatt of electric power is generated. It supplies electric power to all processes equipments in Ammonia complex and also supplies steam to the main steam line to cater to the entire process steam requirement.

CPP consist of two boilers which are capable of producing 60 tones of superheated steam per hour with a temperature of 520 degree Celsius and a pressure of 110 ata, this steam is supplied to all major steam line.

In CPP mainly four steam lines are used. They are classified as follows;

- High pressure steam lines -110 ata

- Medium pressure steam lines-42 ata

- Low pressure steam lines-12 ata

- Exhaust steam line-3.5 ata

Steams thus obtained are used for driving turbines, chemical process requirements, heating purposes etc.

In CPP nine turbines are used. Steam inlet of 110 ata (HP) is used for driving Turbo Generator (TG), which generates Six Megawatt of electric power. All other turbines are used as prime movers for the pumps. Steam inlet of 42 ata is used for driving these pumps.

•   BOILER FEED WATER SYSTEMS

In water management system, which supplies pure water for the jproduction of steam, the water provided should be de-mineralized and de-oxygenated .The pH level is maintained at 9. Boiler feed water system includes:

1) De-Mineralized Water Tank (DM Water Tank)

The DM water supplied from the DM plant is stored in the DM tank. The water for the boiler is stored in this DM tank. A constant water level is maintained in this. A steam driven pump and a motor driven pump are used for pumping the DM water from tank to the next stage, which is de-aerator

2)Deaerator

Before the water is supplied to the boiler, the oxygen content should be removed. This is done in this equipment. The temperature of the water is raised 110 degree Celsius. The level control valve is used to control the water level in the deaerator. Level switches for high and low levels are also incorporated in the deaerator. The water is pumped from the deaerator to the next stage.

3) Dosing

Dosing is a process which is done to maintain a constant pH of 9 in water before it is supplied to the boiler. This process has been undertaken along with the suction of the pump. Ammonia is used for this purpose. The dissolved oxygen is removed by dosing Hydrazine. Both Hydrazine and Ammonia are added to suction input of boiler feed water pump.

•   BOILER AUXILIARIES

1)	Economizer

Water from the boiler feed water pump reaches the economizer. Here the temperature is raised to about 210 Degree Celsius. This is done to enhance the Bteam generation. The economizer inlet is connected to feed pump and the out let is connected to steam drum.

2)	Boiler Drums

Boilers consist of two cylindrical drums which are placed one above the other which are separated by tube lines. The upper drum is called Steam drum and the lower one is called Mud drum. The super heated steam of 110 ATA is obtained from the steam drum. Heat exchangers are used for the exchanging flue gas temperature to the steam. Heat exchangers are connected to the steam drum

3)	Flue Gas Exhaust System

This system provides a negative pressure inside the furnace. It is [provided before the stack. The flue gas is expelled through the stack using Induced Draft

(ID) fan. Rate of removal of flue gas is controlled by using ID fan, so as to provide a t negative pressure. The negative pressure concentrates the flame throughout the furnace. | The burned fuel is removed from the furnace using ID fan through stack. The harmful

gases are reduced and exhausted through the stack to the atmosphere.

. 4) Super Heater

The  saturated  steam  from the  steam  drum  flows to  Low Temperature Super Heater (LTSH) located in the duct connected between boiler banks and economizer, then to platen super heater or directly from drums to platen super heater located in the upper furnace area. The steam then flows to final super heater through a spray type de super heater and then passes on to the main steam line. In case of single

stage super heater, steam from the drum flows to super heater. The steam then flows to

■

plain steam line through spray type de super heater

^ 5) De Super heater

De super heaters are provided in the steam line between super heaters or between super heater and main steam line to permit reduction of steam temperature when necessary and to maintain the temperature at designed values with in the limits. Temperature reduction is.accomplished by injecting spray water in to the path of steam through a nozzle. The spray source is from the boiler feed water system. It is essential that the spray water be chemically pure and free of suspended and dissolved solids, containing only approved volatile treatment material in order to prevent chemical ■deposition in the super heater

I

,6) Combustion

The furnace oil is the fuel used for the combustion. Oxygen needed for burning the fuel is delivered by FD fan in to furnace from atmosphere. The air is pre heated using steam coil air preheater. The air is further heated by the heat of exhaust flue gas in the tubular air pre heater. The fuel for combustion is injected into the furnace by using oil burner. Four oil burners are provided to get a uniform flame distribution inside the furnace. The oil burners use steam at 12 ATA for atomization of the fuel oil. Atomization results in fine spray of oil, which leads to complete combustion.

7) Soot Blowers

Soot coated on the inside parts of the boiler have to be removed periodically. This is done by soot blowers. For this purpose two types of soot blowers are used, rotary soot blowers and long retractable soot blowers.

•   BOILER STEAM SYSTEM

. Steam of 110ATA with a temperature of 520 Degree Celsius is provided and supplied to the main steam line by the boiler steam system. The feed water enters the economizer and is heated to about 210 Degree Celsius. The water is supplied to

I the boiler at the steam drum. A particular water level was maintained in the steam drum.

i For maintaining the required water level during changed boiler load conditions, a boiler drum level control valve is used. The water reaches the lower mud drum through water wall tube lines. The water changes to steam at these tubes. In the steam drum, this mixture of water and steam gets separated in the steam separator, and the water is again

; fed down through water wall tubes. This process is repeated and constant steam level is maintained at the steam drum by the drum level control scheme. This steam has to be

.superheated. The steam then flows into the Low Temperature Super Heater (LTSH) where the temperature increases and condensates are removed. Further steam is passed through the Platen Super Heater (PSH) where the temperature of steam raises around 600 degree Celsius. This temperature is reduced at the de super heater, where the water is I sprayed for this purpose. The final super heater is used to maintain a temperature of 520 degree Celsius. The superheated steam with temperature of 520 degree Celsius and pressure of 110 ATA is supplied at super heater header.

The water supplied at the steam drum is mixed with the phosphate. This is also a type of dosing for reducing the hardness of water. Tri-Sodium phosphate is used for this purpose. It heaps to increase the pH and make the hard water loft.

PSH -  Platan Super Heater FSH -   Final Super Heater OBD - Observation Door RSD - Rotary Soot Blower CAD - Circular Access Door IH   - Inlet Header OH - Outlet Header

LTSH - Low Temperature Super Heater

El     - Economiser 1

E2     - Economiser 2

TAH - tubular Air Preheater

SCAPH - Steam Coil Air Pre Heater

AD     - Access Door

LRSB - Long Retractable Soot Blower

•   BURNER DATA SHEET

Project: 2*60 TPH. Boiler-FACT, Udyogamandal.

\ Boiler Data

Number of boilers	-2

Capacity	-60 TPH

Furnace Data

Furnace width	-4877 mm

Furnace Depth	- 6401 mm

Type of furnace operation -Balanced Draft furnace

Burner

Number of burners/boiler - 4
Type of burner	-Oil fired burner

Type of fuel	- LSHS/furnace oil

Type of atomization      - constant pressure steam

atomization.

Burner Location

Burners are located on the furnace front wall at two elevations with (wo burners in each row. It is proposed to provide common wind box with bottom entry having two burners in each elevation.

The cooling air shall be available at pressure of at least 250mm WG above the maximum surface pressure.

Igniter - 1.20.000 btus/hr LPG(propane) Type of igniter - gas electric with ionic flame monitoring system.

Number of igniters - 1/Burner Igniter capacity   -0.038*10A6 LPG pressure at igniter   - 0.35 Bar

Scanner

Number of scanners - 1/Burner

Type	- I.R.. with self checking feature.

boiler Operation

The boilers installed in CPP of Ammonia Complex are furnace oil fired, balanced draft type with four oil burners in two tier formation. The output steam ■ parameters are 525 deg. C, 110 kg/sq.cm. The operation of this boiler can be broadly \ divided into:

f  Preparation for start-up

- Start-up of Boiler (Lighting of Burners)

- Pressurization and attaining rated parameters *•   Loading of Boiler.

Preparation for start-up

Prior to the lighting up of the boiler, the boiler has to be totally, boxed up in the feed water, steam, and air / flue gas sides, i.e., all maintenance work should be made over and all the manholes, etc. should be closed. The boiler drum shall be filled with adequate amount of feed water (de-mineralized water). The ID and FD fans | shall be made run with air flow more than 30% of rated full load value. The steam coil air j pre-heater shall be put in service so that hot air enters the furnace and leaves through the ! stack (chimney). ID fan speed shall be adjusted to get proper negative pressure in the j furnace. All boiler drum and steam line vent valves should be kept open. All the burner j guns should be cleaned and fixed in position. The furnace oil shall be heated up in the oil j pump house and the hot furnace oil shall be circulated upto boiler trip valve and returned j back. This is for maintaining required temperature of Furnace Oil to the burners. Oncej the required temperature of Furnace Oil has been achieved and all other boiler trip conditions have been reset, and the boiler is ready for light-up.

Btart-up of boiler

Once the preparations for start-up are over, Boiler purging start command should be given. This will initiate a 5 minute sequence whereby it is positively (ensured that any unburnt material inside the furnace has been properly evacuated and the furnace is safe for introducing flame. (The steady air flow is maintained during these 5 [minutes by FD/ID fans). Once purging of the boiler is over, the trip valves (Ignitor Gas itrip valve, Atomizing Steam trip valve and Furnace Oil trip valve) are kept opened.

The first step in lighting up the boiler is the lighting up of ignitor. lEach burner gun is provided with a pilot ignitor which uses LPG for burning. Upon giving Ignitor ON command, an electric spark plug initiates the ignitor firing. Upon [successful firing of LPG, the ignitor flame scanner gives positive signal and the electric Ipark is withdrawn and LPG valve of that particular burner stays on. This will facilitate she lighting up of main burner (Furnace Oil burner). The usual practice is to light up any of the two burners in the bottom tier.

Once ignitor flame is established, the burner start command is fgiven. This will initiate a scavenging sequence at first. During scavenging, atomizing feteam is let to both oil path and steam path of the oil burner gun. This will help in heating ^ip of the burner gun internals (so that when furnace oil is let in later, it does not solidify inside the gun) as well as to do a final cleaning. Once the scavenging is over, the ^scavenging valve (which lets atomizing steam in to the furnace oil path of burner gun) jcloses and furnace oil valve (oil burner trip valve) opens. In this condition, at the burner tip, the furnace oil enters the furnace in a fine spray form (due to atomizing effect of isteam) in front of the ignitor flame which is already present there. The furnace oil spray gets lighted up due to the ignitor flame, and the oil flame gets established. This is confirmed by the oil flame scanner and burner ON indication is received. By visually ^.confirming the healthiness of the oil flame (through view glasses provided on the side of jthe boiler), the ignitor flame is stopped. In this condition, the main flame stays lit, and the

heat of the flame starts getting absorbed by the feed water inside the boiler water walls. Due to any reason, if the main flame fails; we have to again start ignitor, do scavenging of the gun, and then light up again. Once all the oil burners come on line, the ignitor trip valve is closed.

Pressurization and attaining of rated parameters

Once the burner is lit up, it can be seen that the boiler temperature starts increasing. This cannot be allowed to rise beyond some safe rate of rise. For the same, the boiler start-up curves are to be followed. For maintaining the required rate of rise of temperature, it will be required to control the oil flow through the burner, taking care not to reduce the oil pressure below the trip value. Start-up curves are designed keeping in view of the allowable thermal stresses on the boiler pressure parts and their expansion, etc.

Once the water temperature exceeds 100 Degree Celsius, steaming starts and steam starts escaping through drum vents. These vents are gradually closed. The steam produced will then flow through the super heater coils and the super heaters start getting heated up. Steam escapes to atmosphere through main steam start-up vent valve. All the while, the boiler start-up curves are to be followed strictly, whereby rate of rise of boiler pressure / temperature is to be maintained. The rate of rise of steam pressure is controlled by a combination of adjusting oil quantity and throttling of main steam vent valve. As the steaming starts and venting of steam occurs, a close watch shall be maintained on the boiler drum level. The drum level drops and the same shall be normalized by giving feed water so that safe level is always maintained in the drum.

Once the boiler attains pressure of around 90 kg/sq. cm, the quantity of steam vented becomes more and it may necessitate lighting up of one more oil burner so that the required rate of rise of steam pressure can be maintained. Once the main steam temperature and pressure reaches rated values, the boiler is ready for loading.

[Loading of boiler

For loading the boiler, the main steam stop valve (which is the main outlet valve) is gradually opened, and the start-up vent is gradually closed. This diverts the steam flow from escaping to atmosphere there by feeding the steam requirement in downstream steam lines. The steam generation will have to match with the steam requirement in real time. Depending upon the need of the downstream steam consuming plants, the flow varies. If the quantity of the oil fired is kept constant, this will lead to fluctuation in steam pressure, and it may lead to even tripping of the boiler. It is here that the boiler load control comes into action. A closed loop controller always monitors the main steam pressure and sends corrective signals to the oil / air flow controllers. Oil flow is controlled by oil flow control valve and air flow by varying the FD fan speed. As the FD fan speed varies, ID fan also varies automatically so as to maintain safe negative pressure in the furnace. The steam coil air pre-heater is isolated once the exit flue gas temperature goes above 135 Degree Celsius which is the acid dew ipoint.

The oil flow is always limited to the lowest of two values: oil flow permissible for the present air flow or signal from main steam pressure controller. Similarly, air flow is always maintained as highest of the following two values: air flow permissible for the present oil flow or signal from main steam pressure controller. This logic is followed, so that the furnace is never starved for air, which is a potentially dangerous condition. So, while the boiler main steam pressure control system is on auto mode, it can be seen that when steam pressure goes up, the oil flow reduces first, then followed by air flow. And when steam pressure goes down, the air flow increases first, followed by oil flow. For safe operation, it is normal practice to monitor the oxygen [content in flue gas, which indicates the quantity of excess air fed to furnace.

The boiler can be loaded upto around 35 T/hr. with two oil ' burners. Beyond that, the top tier oil burners are also lighted up. To have a uniform

j|jii||iiM«»js^^	■ -

heating up, usually all four burners are lighted up beyond 20-22 T/hr. boiler load. For maintaining steam temperature at higher loads, de-superheater water spray is given between platen super heater and final super heater. This is called attemperation. A closed loop control monitors the main steam temperature and adjusts the feed water spray (attemperator water flow) so as to maintain the main steam temperature.

BOILER PROCESS CONTROL SYSTEM o   INTRODUCTION

The boiler plant installed at Ammonia Complex, Fact, Udyogamandal is mainly meant for producing steam to run the turbine which in turn generates the power required to run the various plants which produces chemicals to be 'used in fertilizers.

Boiler requires special treatment in their control because of the complexity of their numerous controllable parameters and control actions. The requirement for the reliable and efficient operation of the boilers coupled with those of the steam consumers makes the problem of boiler control sufficiently complicated. The consumer consumes steam at specified pressure and temperature and by a specified (amount per unit time.

Basically the boiler plant consists of a furnace process and a steam vessel that handles the pressure and the temperature. For the boiler plant to operate well the furnace process should have maximum efficiency-this in relation to fuel and air inlet supplies as also the furnace pressure. The general types of boilers are drum type ones and the water level in the drum should be with in the prescribed tolerance limit. Thus the variables that need to be controlled for operation of boiler plant are fuel, air, feed water, fuel suction and draught, coolant supply for temperature control of de super heaters etc.

Boiler control is accomplished by means of two systems:-

- The burner management system

- The combustion control system

- Programmable Logic Controller (PLC) based Burner management system which supervises the control of the fuel burning equipment and provides all the monitoring facility for safe and smooth startup and shutdown of the boiler. '

- Distributed Control System (DCS) based combustion control system, designed to maintain the header steam pressure constant under any boiler load. Flow of fuel and combustion air is controlled by master steam pressure controller. Air rich conditions are maintained to ensure optimum combustion under any load change. After through and exhaustive study of these two systems, we suggested a few modifications aimed at better more efficient and safer operation of the plant. We brought about changes in the program and advised practical circuits for implementation in the plant, for this purpose.

o   BURNER MANAGEMENT SYSTEM

The burner management system must essentially provide automatic sequence of operation of connected boilers during start up and its shutdown. It should also indicate the operator the existing states of various elements of fuel burning equipment. The system must indicate safe shutdown procedures as and when an unsafe operating condition is detected.

o  COMBUSTION CONTROL SYSTEM

The combustion control system is designed to feed the fuel and air to the furnace to produce the system at a given constant pressure depending on the requirement of boiler load. The set point of the fuel and air controllers is adjusted and a corrective output signal is produced.

Ultimate aim of combustion control system is to deliver steam at constant pressure as per demand economically by effective utilization of fuel. Optimal combustion

takes place in slightly excess of air and also there exists a definite ratio between air and fuel in a combustion system. Thus the four inputs to combustion control system are:

■

- Fuel flow

- Air flow

- Present steam pressure

- Percentage of oxygen

There are two outputs:-one for opening of fuel flow control valve and another for forced draught fan. These then form the set point of fuel and air controllers and a corrective signal is produced.

| ■ | THE BURNER MANAGEMENT SYSTEM |
| --- | --- |
| > START UP SEQUENCE ) |  |
|  | The BMS supervises the admission of fuel and air into the boiler , |
| ..and it also provides all the ON/OFF control and monitoring necessary for safe and |  |
| [smooth start up and shut down for the boiler. The start up and shut down is done in a |  |
| sequential order. The sequence is as follows; |  |
| ♦ Furnace Purge |  |
|  | Before any fuel firing can take place (initially or) after a Master |
| Fuel Trip, a satisfactory furnace purge cycle must first be completed. For a satisfactory |  |
| furnace purge, the following are essential. |  |
| \ 1} | Establish Logic power and power for Ignitor, Scanner and illumination to |
|  | BMS. |
| 2) | Establish proper drum level ; |
| 3) | Put ID fan into service ■ |
| 4) | Put FD fan into service ! |
| 5) | Establish proper purge air flow by manually increasing the air flow until a |
|  | minimum of 30% of full load air flow is established |
| 6) | Ensure scanner shows no flame |
| 7) | Start furnace purge cycle by depressing the "Purge Start" push button |
|  | after "Purge Ready" light comes on indicating that all the purge |
|  | requirements are satisfied |
|  | ._. |

Note : 1

The "Purge Ready" light will not come on unless all the following requirements are satisfied.

- ID Fan is operating

- FD Fan is operating

- Air Flow greater than 30%

- Drum level is not very low

- Furnace pressure not very high

- Emergency trip push button not depressed

- All scanners Show no flame

- HOTV closed

- All OBTV closed

- Any Burner Air damper Open

- Furnace pressure not very low

- IGTV closed

When the flame purge cycle is started, "Purging" light comes on and remains on during the entire five minutes of purging cycle.

Note: 2

At the end of furnace purge cycle(five minutes)

. 1) The Boiler Trip (or Master Fuel Trip) and purging light goes out 2) The "Purge Complete" light comes on

♦	Ignition Start

After purge complete, any ignitor can started provided "Ignitor start Permit" light is ON. The ignitor start permit light is on when the following requirements are satisfied.

- NoMFT

- Ignitor Gas Pressure is not low

- IGTV open PB is depressed

- Burner Air Damper open

Pressing the IGTV open push button Ignitor Start Permit light comes on and will open the Ignitor Gas Trip valve.

After the Ignitor Gas Trip valve is opened when the Ignitor proves no flame, the "Ignitor ON" push button is pressed energizing the mixer block (Air & Gas) solenoid valve for 10 seconds allowing the mixed gas flows through the Ignitor. Now the Spark Plug produces spark and mixed gas fired by the sparks.

During the Ignitor trial time of 10 seconds, if the Ignitor flame is not established, then the Ignitor Gas valves closes and Ignitor has to be re-started.

♦	Heavy Oil Start

For the "Heavy Oil Trip Valve" does not open, check to see that;

- Oil Pressure is OK

- NoMFT

- Oil Pressure not very low

- Atomizing Steam Pressure not very low

tOil re-circulation must be done before opening the HO Trip Valve.

♦  Oil Firing

Once the Ignitor is in service, and the Heavy Oil Trip valve is opened. Oil firing can be started by opening the "Oil Burner Trip Valve", proceed as follows;

- Oil Gun to be Engaged

- Burner Air Damper to be Opened

- Atomizing Steam Manual valve opened

- "Oil Start Permif light is on, indicating that permissives are satisfied to open the Burner Trip valve by depressing oil burner on push button (ie OBTV 1 is ON). Similarly for other three Burners.

Note : 4

If the "Oil Start Permit" light does not come on, check to see that;

- HOTV opened

- Atomizing Steam Pressure not low

- HO Manual valve is opened

- Atomizing Manual valve is opened

- HO temperature is not very low

- Scavenge valve closed

- Ignitor is ON

When Oil Burner on push button is depressed the Atomizing Steam valve is opened first. Then, Oil Burner Trip valve will be opened and indicated by the light coming on.

The first scanner must prove flame at this time. If the flame is not proven with in 10 seconds of the opening of the Oil Burner trip valve, then the OBTV will be closed and the scavenging to be started by depressing scavenging valve open PB

and automatically stopped after 3 minutes . if the scanner proves flame, then OBTV-remains open. Similarly for OBTV-2, OBTV-3& OBTV-4.

Note : 5

The Burner should remain in the " Low Fire Start" position until steam is delivered to the system.

Any one of the following conditions will cause a Master Fuel Trip to occur and results in the immediate shut down of all fuel in service, which necessitates a Furnace Purge Cycle completion before any fuel firing may be re-instated.

- Furnace Pressure very high

- Drum level very low

- ID Fan not operating

- FD Fan not operating

- Emergency Push Button initiated

- Air flow less than 30% of full load

- All scanners show no flame

The flow chart for the whole sequence is given below;

FLOW CHART

START

Close HOTV and IGTV if Open

STOP

Indicate Purge Ready

Press Purge Start Push Button

O

Indicate Purging

Purge Complete Permanently

| Indicate Igniti | an Start Ready |
| --- | --- |
| Press Ignition | Start Push Button |

Indicate Oil Firing ready Signal

Indicate HOTV Open Permit

Indicate Ignition Established Signals

Press HOTV Open Push Button

Indicate HOTV Open Permanently

Press OBTV Open Push Button

Indicate IGTV Ready

.Indicate IGTV Open Permanently

Press IGTV Open Push Button

Indicate OBTV Open Permanently

| Burner on Indication |  |  |  |
| --- | --- | --- | --- |
|  | Close IGTV |  |  |

STOP

> CONTROL SEQUENCE

Burner management is the control of fuel burning equipment required on steam generator for safety operation. In the early days of burner management, it was carried out by field wiring of various devices in series and parallel to perform the required logic sequence and safety interlocks.

The burner management system provides proper sequence of equipment during the normal startup, operating and shutdown procedures. In addition, it provides for a fuel trip during adverse boiler or burner operating condition. This is accomplished through the use of programmable logic and various interlocks.

In the boiler system installed at FACT, Udyogamandal, the burner management system serves the boiler to fire through four independent burners. Each burner is equipped with main oil gun for firing steam atomized heavy oil. It is also provided with a gas ignitor, flame scanner for scanning the flame.

The burner management includes different controls, following below;

- Purge Control

- Ignition Gas Trip Valve Control

- Ignitor 1,2,3,4 Controls

- Heavy Oil Trip Valve Control

- Oil burner Trip Valve 1,2,3,4 Controls

. •	Scavenging Trip Vah e 1,2,3,4 Controls

Each of these controls is maintained by certain conditions. So this gives the complete management of the burner. This is carried out by means of the programmable logic controller. If any one of these condition is wrong the PLC can take the necessary action according to the software installed on it.

The conditions for each section are given below.

Purge Control

Before a fuel firing; after a master boiler trip, a satisfactory

furnace purge cycle must be completed. Purging is nothing but a cleaning of the furnace. During these cycles all the fuel valves are closed, only the FD and ID fans are operated, so the ID fan takes away all the air (and possible unburnt / combustible gases) from the furnace through the stack. For a satisfactory furnace purge, the following are essential:

- ID fan is ON

- FD fan is ON

- Air Flow greater than 30%

- Drum Level is not very low

- Furnace Pressure is not very high

- Establish proper drum level

- All scanners show no flame

- All Oil Trip Valve are closed

- Heavy Oil Trip Valve is closed

- Ignition Gas Trip Valve is closed

- Furnace Pressure not very low

When the furnace purge cycle is started, "purging" light comes ON and remains on during the entire five minute of purging cycle. After this five minute the "purge complete" light comes ON.

Ignitor Start

After purge is completed, any ignitor can be started, provided "ignitor start permit" light is ON. The ignitor start permit light is ON when the following requirements are satisfied:

- No Master Fuel Trip(MFT)

- Ignitor Gas Pressure is not low

- IGTV open press button depressed

- Burner Air Damper open

Pressing the IGTV open push button"Ignitor Start" permit light comes ON and will open the Ignitor Gas Trip Valve (IGTV). After the IGTV is opened when the ignitor provides no flame, the "Ignitor ON" push button is pressed thus energizing the mixer block solenoid valve for 10 sec allowing the mixed gas flow through the Ignitor. Now the spark plug produces spark and mixed gas fired by the spark. During the ignitor trial time of 10 sec, if the ignitor flame is not established, then the ignitor gas valves closes and ignitor has to be restarted. When ignitor flame is established, "Ignitor ON" lamp gets lighted up and further oil burner starting permissive is given.

Heavy Oil Control

By this section we can control the flow of furnace oil to the burner. For opening the heavy oil trip valve some conditions must be satisfied as given below:

- Oil pressure is in the required range

- No MFT

- Atomizing steam pressure not very low

- Oil temperature is in the required level

The oil must be recirculated before the opening of the heavy oil trip valve

Oil Firing or OBTV Control

Once ignitor comes into service, and the heavy oil trip valve is opened, oil firing can be started by opening the "Oil Burner Trip Valve" which gives oil to the individual burners. The conditions for oil firing are given below:

- Oil gun to be engaged

- Burner air damper to be opened

- Atomizing steam manual valve opened

- Corresponding Ignitor is ON.

"OiJ Start Permit" light is on, indicating that conditions are satisfied to open the Burner Trip Valve by depressing "OBTV 1 ON" push button, similarly for all other three burners. If the "Oil Start Permit" light does not come ON, check the following:

- HOTV opened

- Atomizing Steam Pressure not low

- Heavy Oil manual valve is opened

- Atomizing manual valve is opened

- Heavy Oil Temperature is not very low

- Scavenge Valves are closed

- Ignitor is ON

When "Oil Burner ON" push button is depressed, the atomizing steam valve is opened first. Then oil burner trip valve will be opened indicated by the light coming ON. The flame scanner must prove flame at this time. If the flame is not proven with in 10 sec of the opening of the oil burner trip valve, then the OBTV will! rbe closed and the scavenging to be started by depressing "scavenging valve open" Push

button and automatically stopped after 3 minutes. If the scanner shows flame, then OBTV 1 remains open. All the OBTV's are operated in the same way.

Scavenging

It is the process of firing out the heavy oil inside the burner gun after a main flame trips. The furnace starts by firing LPG and goes on working by firing the heavy oil. So after a main flame trip the furnace starts with LPG, before this all the heavy oil must be fired.

When "scavenging valve ON" Push button is pressed it check for the following:

- Ignition start command

- All the OBTV's are closed

- All the scanners shows flame

The logic diagrams for all these sections are given below which shows the exact location of the various burners in the two boilers, position of various valves etc.

Hj£hs PmjsuAl

7\

ho (rOfl   ^

To Gut as f 5

IGffV

pilof vfi&£

LPOi

firryfllo7rus?rij fr,p)/aluj

HttPv —> HeA*y Of$ Vrfp \ZcduJ-lot?/       Tjfjkol Otctp ?rfp Va$iA?

I

A.	Pilot valve

B.	OBTV

C.	ATV

D.	Damper

E.	Scavenging valve

F.	Oil Manual valve

G.	ATM manual valve

H.	igvv

I.	IGTV
J. HOTV

1.  pfaofQlfiS

%■   CO MQVSflOti PtlR

H-  FO/LSH5

> VERBOSE LISTING

BOILER LOGICS

1. Boiler Trip Settings

The following conditions will bring about a 'Boiler Trip', which logically means that Purging is required before re-starting.

Drum Level Very Low Drum Level Very High Furnace Pressure Very Low Furnace Pressure Very High Air Flow < 30 % ID Fan Trip FD Fan Trip

: 20 %( at rated pressure) : 80 %

: -250mmwc, 3sec. : +330mmwc : 26 T/Hr, 5sec.

2. HOTV Trip Settings

HOTV Trip will also physically bring about a Boiler Trip, but logically this does not demand a Purging before starting up again.

HO Pressure Very Low	: 2.3 Kg/cm2

HO Temp Very Low	: 80 deg. C

Atomizing Steam Pressure Very Low : 4 Kg/cm2

3. Burner Trip

This is for individual burner trip. However incase all four burners, trip, it will be physically a Boiler Trip but logically a Burner Trip only.

Flame Intensity	: 60 %

| 4. 'Purge Ready'Permits |  |
| --- | --- |
| All 'Boiler Trip' conditions reset All Main Flames off All OBTVs close HOTV close IGTV close |  |
| 5. IGTV ODen Permit |  |
| Purge Complete Ign. Gas Pressure Very Low |  |
| 6. HOTV Open Permit |  |
| Purge Complete All 'HOTV Trip' Conditions reset |  |
| j 7. OBTV Open Permit |  |
| Purge Complete HOTV Open Ignition On Oil Manual Valve Open Scavenging Valve Close Atomizing Steam Manual Valve Open Atomizing Steam Pressure not Low |  |
| 8. OBTV / ATV Open Command Sequence |  |
| OBTV Open Permit ¦ ; Oil Gun Engaged ->ATV Open Command OBTV Open PB Operated ¦ |  |
| j ATV Open Command ¦->OBTV Open Command \ ATV Feedback ¦ |  |

9. Scavenging Valve Open Permit

OBTV Close Ignition On

BOILER AUXILIARIES LOGIC

1.	Trip Settings of all Auxiliary Turbine

All these trips are operated through the local control panel. Turbine Oil Pressure Very Low    : 2.5 Kg/cm2 Gear Box Oil Pressure Very Low   : 0.8 Kg/cm2 Oil Temperature Very High deg. C : In the range

57-65 .

Over Speed	: Approximately

+ 10%

2.	Trip Settings of Boiler Feed Pumps

Deaerator Level Very Low	: 17 % (approx)

Suction DP Very High	: 0.8 Kg/cm2

Bearing Temperatures Very High   : 80 deg. C

This trip is implemented through the local control panel for Turbo Driven Pumps and through PLC for Motor driven Pump.

Additionally, for BFP-3 (motor driven), Lube Oil Pressure Very Low trip is provided.

3. Deaerator Level Alarms

Deaerator Level Low Deaerator Level High Deaerator Level Very High

18 %(apporox) 85 %(apporox) 94 %(apporox)

4.   Auto-Starting of Standby Equipments

i. Boiler Feed Pump

Pump   will   start  automatically   when   the   following conditions are satisfied:

a.	Local/Remote Switch in Utility Desk is in
'Remote'

b.	Auto/Manual Switch in Utility Desk is in 'Auto'

c.	Local Control Switch is in 'Auto'

d.	'Ready for Start' indication is available at LCS

e.	Pump Discharge common header pressure

is < 120Kg/cm2 or both turbo driven pumps are tripped / not running.

ii. Fuel Oil Pump

Pump will start automatically when the following conditions are satisfied:

a.	Local/Remote Switch in Utility Desk is in

'Remote'

b.	Auto/Manual Switch in Utility Desk is in
'Auto'

c.	Local Control Switch is in 'Auto'

d.	'Ready for Start' indication is available at LCS

e.	Any one of the turbo driven pumps is tripped / not running.

iii. DM Water Pump

Pump  will  start  automatically  when  the  following conditions are satisfied:

a.	Local/Remote Switch in Utility Desk is in
'Remote'

b.	Auto/Manual Switch in Utility Desk is in
'Auto'

c.	Local Control Switch is in 'Auto'

d.	'Ready for Start' indication is available at LCS

e.	Turbo Driven DM Water Pump is not /tripped.

> PRESENT IMPLEMENTATION OF INTERLOCKS & PROTECTION

In the existing control systems, the interlocks and protections are realized by means of electromagnetic relay based system. Here abnormal plant parameters are sensed by pressure switches / temperature switches / limit switches / flame scanners, etc. and reliable contacts are fed to the relays. The relay contacts are wired according to the above logics to derive certain output contacts. These relay output contacts in turn drive the various systems to allow starting the turbine, trip the running turbine, start auxiliary equipments etc. as per the logic.

The electro magnetic relay based system has the following drawbacks;

- Since entire logic is hard wired between different relays, the reliability is low.

- The probability of plant getting affected due to relay failure is more.

- The relay, interconnecting wiring etc. takes up more space and also makes trouble-shooting difficult.

- If any change in logic is required, it is very difficult to implement since lot of wiring will have to be changed physically.

> PROPOSED MODIFICATIONS OF THE INTERLOCKS & PROTECTION OF THE SYSTEM

In the view of inherent drawbacks of electromagnetic relay based system, it is proposed to replace the logic implementation using PLC's.The PLC programming based on the ladder diagram & details explained later.

After careful study and analysis of the boiler process control system installed at Ammonia Complex, FACT, Udyogamandal, we suggested a few modifications for better and more efficient operation of the plant. Some of the suggested modifications were very simple and did not require much attention while some others needed immediate attention.

Some modifications suggested include;

- FD fan trip subsequent to ID fan trip.

- Intercoupling of PLC & DCS.

- Ratio bias controller.

(1) FD Fan Trip Subsequent to ID Fan Trip

A rather simplified arrangement of the boiler process control system is as shown

Stack

ID Fan

Air

Reg

ister

Furnace

FD Fan

Air from Atmosphere

Here, air required for combustion is forced into the boiler from the atmosphere by the Forced Draught (FD) Fan. After combustion, the flue gases are thrown out to the atmosphere through the stack, by Induced Draught (ID) Fan.

Now suppose, due to some reason, the ID fan gets tripped while the FD fan goes on working. Then, the gases accumulate with in the boiler developing very high positive pressures, which may damage the boiler and, eventually, lead to the collapse of the whole system. So for proper working of the boiler, it is essential that the FD fan gets tripped subsequent to ID fan trip. Also ID fan should run subsequent to FD fan start-up.

In the boiler plant at the Ammonia complex, no such

interlock exists to cause the same, at present. Hence operational facilities are to be incorporated for this purpose, as suggested by us, to ensure better safety of the plant. This could be done, by just modifying the PLC program. With a flag which indicates ID fan trip in front panel for PLC.

(2) Intercoupling of PLC & DCS

In the existing system, PLC & DCS are two different

sections, completely independent PLC, which monitors the existence of any unfavorable situation, work with digital values. DCS aims at continuous operation and hence, work with analog quantities. Now these two have to be coupled.

To illustrate the present situation, consider the following

examples. The airflow should always be maintained to some value corresponding to the load required. This value should be >30% for successful working of the boiler. If the airflow becomes <30%, the PLC should operate to trip of boiler. For this purpose, two flow transmitters have been installed FT2157 & FT2158, one for DCS & other for PLC.

FT2157

Range 0-86.2 T/Hr, 4-20 mA

DCS

The above arrangement is for air flow indications & control in DCS.

FT2158

\

amplifier

PLC

A/D Converter

Digital I/P

If air flow becomes < (86.2*30/100) T/Hr the trip amplifier is

activated.

The need for two such transmitters could be well avoided if we have accurate repeater or dual circuit like this.

DCS

Current

Repeater

(Dual)

\

PLC

The current repeater will have two outputs. It just duals the input and this is given to the DCS & PLC circuits, separately. Besides, such an -arrangement leads to reduced costs, eliminating the necessity of two parallel circuits.

An improved version of the circuit is shown below;

Transmitters

Field

Junction

Boxes

Marsha

lling

Do

Individ ual

Process, or card

Advanced

Control

card

| i/p |  |
| --- | --- |
|  | w |

FT A (A/D Converter cards

0/

to final actuating device

field termination assembly

(3) Ratio Bias Controller

The existing combustion control system works perfectly, when all the burners in both the boilers are working. But if one or more burners of a boiler trips, when the boiler is in the combustion control loop, immediately, the oil flow controller, FIC2106 and the air flow controller, FIC2107, have to be taken into the manual mode. The output of FIC2106 has to be reduced to maintain higher 02 level in the flue gas. This is because, if the loop is in line, it will try to keep the same total oil flow through the remaining burners, resulting in increased oil flow in these burners, while the air flow remains the same. This would leads to decreased efficiency.

To avoid such a situation, a modification in the combination control loop is essential and the result is the 'Ratio Bias Controller'.

The proposed Ratio Bias Controller (RBC) would divide the air & fuel, equally amongst the presently working burners. This avoids over loading of some of the burners while maintaining higher efficiency, at the same time. Since RBC demands greater attention, it has been dealt separately.

IMPORTANCE OF PROJECT BASED ON ANALYSIS

Steam is mainly required for power generation, driving the turbo generator and heating installation. For the proper operation of plant an uninterruptible supply of steam is required. So a continuous operation of boiler is necessary. The continuous boiler operation provides higher efficiency by proper controlling methods. So the boiler control process is very essential to enhance the smooth start up and shut down and also provides high efficiency.

The main objective of this project is the complete automation of boiler plant based on BMS. Energy saving by proper control or selective switching enhances efficiency of plant and increase economical benefits. These are depends on many parameters included in this operation. The analysis of boiler plant operation gives a detailed study of plant operation and the present implementation. It also provides methods for future improvement. The findings from the project indicates the importance of project that are explained below.

1. Energy Saving by Selective Switching

The boiler process control can be done either manually or automatically. For the continuous operation, it requires periodic examinations of different conditions to be satisfied for switching purpose. So a person has to be appointed just for monitoring the temperature and pressure and do the switching operations. This is cumbersome duty and wastage of labour. These problems can be avoided by automated switching operation using PLC. This will account to saving of annual energy consumption and reduction in laborer.

By automatic combustion control system it is very easy to meet the requirements of steam demand. When the boiler steam demand is decreases oil demand decreases. This is done by reducing speed of the Forced Draught fan (FD fan) which is driven by turbine blades whose rotating speed is set up adjusting steam input.

It is necessary to maintain a constant steam pressure and uniform furnace draught and supply of air or fuel which can be regulated to meet the changes in steam demand. It is very efficiently done by selective switching process. So the boiler operation becomes more flexible.

The speed of fan is regulated with respect to the steam demand. The supply of air is done through FD fan which helps for complete combustion of fuel and thus avoid wastage of fuel. So the steam demand is satisfactorily meet by adjusting speed of fans (directly proportional to demand).

2. Improve Efficiency

In FACT, the boiler produced steam rate is represented as 60TPH, at 520 degree c. and 110kg. It is a high pressure boiler with high capacity. It provided higher efficiency (output/input - steam/fuel) and high steam rate, ie The high pressure and temperature steam has high heat content so less steam is required for meeting the requirement. So less fuel is needed for obtaining some efficiency, ie It provided high efficiency and leads to less wastage of energy.

Boiler efficiency depends on the following factors, air fuel ratio, soot formation and insulation. The efficiency can be increased by maintaining proper air fuel ratio. This leads to reduce excess flue gases and thus heat losses. Soot formed by boiler operation is removed by soot blowing operation which is periodically run for cleaning the internal parts of boiler. The insulation level must be satisfactorily provided for feed water system to avoid heat loss through water tubes.

The boiler efficiency can be increased by reducing heat loss.

This is done in 3 ways;

- Absorb flue gas temperature by water tubes

- Soot is removed by soot blowers which is periodically run by steam

- To reduce flue gases by minimize excess air or maintain proper air/fuel ratio

The steam produced in boiler is saturated, which is not used in turbine because the dryness factor of steam leaving the boiler will be very low. This results in the presence of moisture which causes scaling of turbine blades. To raise the temperature of steam super heaters are used. It supplies steam at constant temperature at different loads. So super heated steam increase efficiency. The proper setting of arrangement of FD and ID fans improve burning of fuel and achieve higher efficiency.

3. Economic Benefits

In the existing control systems, interlocks for tripping are realized by means of electromagnetic relay based system. Its reliability is low and hard wired structures leads to high insulation or capital cost. It has some disadvantages too. Here error detection is difficult due to complexity in configuration. So maintenance cost is high and also time loss is more due to the wastage of time for repairing hardwire parts. It require more space for installation.

This is avoided by using PLC control. It provides continuous operation and avoid increased rate of energy consumption due to frequent starting and tripping. PLC are programmable according to requirement. So configuration do not affect according to demand. It give reliable and efficient operation for long life time and also provides safety requirements. This automatic control reduces the labour. Recirculation of DM water reduces running cost. By proper controlling of speed of fans and the combustion of fuel, wastage of fuel is avoided. There by expenses reduces and operation is economically beneficial.

AUTOMATION OF OPERATION OF BOILER PLANT USING PLC

Today, automation is moving rapidly towards a true point of central control that resides in the system operator's office. It is becoming increasingly necessary for the system operators to have finger tip control of the process. This has been greatly fulfilled by the use of programming device.

Programmable devices eliminate the need of complex components and the discrete components. They are also more reliable, cheaper and it can withstand harsh factory environments, perhaps the biggest advantages of programmable devices is that their functions are easily changeable by merely changing the program stored in them, there by eliminating need for replacing the whole system. Additional changes can be made incrementally. They also allow interaction with other systems and since their outputs are digital, their working can be easily monitored by computers.

In the world of automation, PLC has become a standard for control. It now not only replaces the earlier relay controls but has taken over many additional control functions. PLCs are used to synchronize the flow of inputs from sensors and events with the flow of outputs to actuators and events. This leads to precisely controlled actions that permit a tight control of the process or machine. This project is devoted to the principle upon which PLCs operate.

Until the last decade control were realized through the discrete relays. Relays, though simple, because of these discrete nature and the need for them to be hard-wired for their operation become cumbersome and unfit in cases where a lot of conditions are to be satisfied to achieve automatic control when the system requirements change, the relay wiring has to be changed or modified. In an industrial environment, such modifications are not only time consuming but tedious as well. In extreme cases, such as in auto industry, complete panels have to be replaced as it is not economically feasible to old panels with each model change over.

Bigger the process more is need for a PLC. We can simply program the PLC to count its inputs and turn the solenoids on for specified time. Used in industrial and commercial applications, PLCs act as controllers for machines and processes. They monitor inputs, make decisions and control outputs in order to automatic machines and processes. A PLC is a computer designed for using in machines. Unlike a computer, it has been designed to operate in the industrial environment and is equipped with special inputs or outputs and a control program language. Initially the PLC was used to replace relay logic, but its ever increasing range of function means that it is found in many more complex applications.

As the structure of a PLC is same as those employed in computer architecture, it is capable of performing not only relay switching tasks but also other applications such as counting, calculating, comparing and the processing of analog signals . In this project, automation of boiler process system is done using PLC. The ladder diagram technique of programming PLC has been utilized. The implementation of this system would replace existing permanent hard-wired relay system by programmable system varied according to the requirement make the system more reliable and upgraded in future.

LADDER DIGRAMS

Boiler Logics

OOteOO

tooccoo;

000

10.00 Dr_Lvl VLo -(\-

00K01 (00OCO2;

Dr_lvl_vi

0.21

DrJ-vl_VL I 10.Pi    OrtviV.h

000:02

(000204!

Drum level 0.22

Df_Lvl_V. 1002    Furnaceprevl

—o-

000C03 tQQOMS!

Furnacepr

0.53

Furnacepr 10.03    Fumacepre.v h

WK04 (OOKOfl!

Furnacepr 9*4

Furnacepr 10D4    airtlo#<30%

-o—I

ooo:o5

(0OOG101 ailtcwKSO 0.05

air$ow*30 10.25    IDfantrip

000C06 (0000125

I Df anli is

o.:<3

IDfantrip 1006     FDfantiip

—o-

O0OCO7

(0or>:i4)

FOfantnp

0.0O

FDfantnp 10.27     SoilsrTrip

-o	1

b05«

Dr_Lvl_VL 0.31

-H I—

BoilerTno

Drum level

0.2

Furnacepr

0.23

Furnacepr

0«4

I

artow-30 O.DS

IDfantrip

o.:<s

000:10

(O0O022:

FDIantrip 0.2-7

11.00    HOPreV.L

000:11

t000C24:

r-OPmV.L
093

HODreV L l.?:2i    HOTempV.L

000:12 1000:26:

HOTempv

0.03
	1 I

HOTempV

11.02     ATO.STEAMPREV.L

-o	1

ATO.ST=

ATO.STE

000013 (000028!

0.07

11.03     HOTVTnp

-c>

M74

HOPreVL
0 08

HOTVTnp

HOTempV 00-3

000C16 (000032)

ATOSTE 0,10

11,04    BurnertTrip

000317 (0000341

Bumsf Ilia .  0.11

' Burned TrI |

1135    Burner2Trip

000018 (000C38)

Ixirner2fla

too

Burner2Trt 1 H08    8urnef3Trip

000019

(000033) burnerjfia 1JG1

Bum«3Tri |

' 11.27    Bumef4Trip

1.D1

Burneclfla bumer2Ba bumerjfla fcurner4l!a
* 02          1.03          1 04          1 05
	1 I	1 I	1 I

000020 (OOOO+Qj

OOOS23 (000045!

Ixirner4fla

0.10	0.11

Buriier4Tn | 12.00    AllFlaneFal

t a055

AIIFIaroeF

12.01     AJOBTVOose

a056

O—I

000024 (000050;

ofctvlcicse cttv2dose obtv3ticse Disclose

1.06

1 I

AilOBTVC |

12.02     HOTVC10S6

—o

a057

000025 (000052!

hOTVctoS

1.07
	1 I

HOTVctoS| 12.03     IGTVctose

aOH

000028 (000054)

000029

tOOOHOi

IGTvciose

12 03

1301	10.02

H I	1 t-

1007	1200

BoiierTrip AlflameF AI08TVC HOTV'clos IGTvciose 1.08        7IM001

^

IGTvciose I 12.04    PurjeRdyPermit

—O	1:

aM3

■

PurgeRdy 12.05    PurgsStar.GsKen

-O

afi$4

000031 lOOOMH

PurgeStart

1204	12 05

its

001

PurgeRdy PurgeStan

CO0C12 (OOO0-56J

TMC01

12.06    Purge Complete

a070 a073 a»3

000335 .C00M6:

Purse Co 12 07    lgn_gjsore notlo*

Ignjaspr

lgn_gaspr

0O0S3S (000070!

12 07

13,00    IGTVopenPermit

000039 .000273)

Purge Co  lgn_gaspf
2.06	rira

IGT\'xen 1321

HOWopenPermit

000042 (000C76!

000043 (000076)

Purge Co  HOTv'Trip 110

—1 1

IGN_.cn 1.11

HOTVope
	13.22

Ign.ON

i aOW »112

Ign.ON

13.23    OiLmanuatVafveOPE

Oitnanua

13,05
	1 I

PartO'JL

13.06

o—

000044 (000230}

0O0C45 (0000-32:

000346 <000237)

000048 (000092;

OlLmar.ua
2.00

13 02

13,03

SCAVEN

1.C«	12 08

h-^Hr	1 I-

HOTVctos Purge Co Ign.ON

13.04         2.01          2,02
	1 I	1 h

SeavergV ATOM.3  ATOM ST PartOUt.
2.03	1306

OILmanua | 13.04    ScavengVaiveClose

3c3vengV 13 35

a057

PatOUt OBTV

aOSQ

QBTVOpersPermit

aOS3 aS95

OBTVOpe 1307

>BTVOpenP3presse

a097

000050 .OOOffio

000251 1,000099;

000052 (000 f015

OBTVcpe OBTVOpe
■J.06	2,04

13,07

14 03

JBTVOoe QtlGurtEn OBTVOoe 2.35

14 01

ATVopenF

14.00

OBTVOpe I 14 DO    ATVOpenCommand

• 1B1

ATVOpen

14.01

ATVo&ened

a'02

ATVopene I

14 02     OBTVopenCOMMAN

-O	Q

a!05

OOD054

,000105!

ATVOpen ATVopene OBTVctos

14.02

OBTVope

TIM

DBTVope

30X55 (000107)

TIM302 —I 1-

OBTV'CtoseCOMMAM
-0

000358 (.300110;

0002= ? (000112)

•tttvlclcse 1302

I—I I

Sumertfla

14 04

OBTVclOS I 14 04    OBTV1 close

at 13

OBTVioo 14 35

ScavVatveOcen

Seavvak*

laiON    OBTVieio

000060 (000115)

ENC

Boiler Auxiliaries Logic

1

000000 (000300)

10.21    TurbineOiPis.V.C-

'300001

coooaE;;

0.02
I	1 h

TurtineGil

10.02 GearBoxOIPre.V.l
—O	1

GearBoxO

000002 .•300034!

0.03

10.03    GtTampv.H

000003

iQOKXje;

004

OlTempv. 10.04   ■ OvefSpeed

000004

OverSpee 10.05    Aux.TurbineTrip

AuscTuftsi

0.32

0.03

0.04

000-05 (000213;

10.08 Deaerator Leveiv t
	r~\

Deaerator

00036 1000315!

0.36 h

10 07    SuctionOPV.H

000007 1/300017!

0.07

SuctionDP | 13.30    BearinjTemo V.H

000308 .'300319!

0 03 h

BearingTs

11.21 LubeQIPre V ITR1P(
	O	MotorDriven)

000039

(000021!

0,25

Lui>eOilPr |

11.02 BoilerFeedTrip
	O-

BoiterFeed

0,06

0.07

300010 .000025;

11.03 DeaeratorLevetLow.AI
—O	a""

Deaerator

1134 DaaeratorLeveHghAl

C>

-aim

000011 (000327;

010

Deaerator

000012

(OOO02S;:

lias    DeasfatorLevelv.rtgh

—Q	.Alarm

000:13

.000231}

1 03

Deaerator | 1^06    BalerFeedPiimp3Staf

000314

(,000:33;

BomTDPu 131

BoferFeed |

—-C?

000315 .000035)

QneTDpu

1,32

FuelOilPu 1200

TD DMwa

DMwaterP

000016 (00O237)

END

StepInstructionsOperandComment0.LD0.00Drum level very low1.OUT10.00Drum level very low2.LD0.01Drum level very high3. ■OUT10.01Drum level very high4.LD0.02Furnace pressure very low5.OUT10.02Furnace pressure very low6.LD0.03Furnace pressure very high7."OUT10.03Furnace pressure very high8.LD0.04Air flow<30%9.OUT10.04Air flow<30%10.LD0.05ID fan trip11.OUT10.05ID fan trip12.LD0.06FD fan trip13.OUT10.06FD fan trip14.LD0.00Drum level very low15. ■OR0.01Drum level very high16.OR0.02Furnace pressure very low17.OR0.03Furnace pressure very high18.OR0.04Air flow<30%19.OR0.05ID fan trip20.OR0.06FD fan trip21.OUT10.07Boiler trip

BOILER LOGIC MNEMONICS

|  | 22. | LD | 0.07 | Heavy oil pressure very low |  |
| --- | --- | --- | --- | --- | --- |
|  | 23. | OUT | 11.00 | Heavy oil pressure very low |  |
|  | 24. | LD | 0.08 | Heavy oil temperature very low |  |
|  | 25. | OUT | 11.01 | Heavy oil temperature very low |  |
|  | 26. | LD | 0.09 | Atomizing steam pressure very low |  |
|  | 27. | OUT | 11.02 | Atomizing steam pressure very low |  |
|  | 28. | LD | .0.07 | Heavy oil pressure very low |  |
|  | 29. | OR | 0.08 . | Heavy oil temp, very low |  |
|  | 30. | OR | 0.09 | Atomizing steam pressure very low |  |
|  | 31. | OUT | 11.03 | HOTV trip |  |
|  | 32. | LD | 0.10 | Burner 1 flame failure |  |
|  | 33. | OUT | 11.04 | Burner 1 trip |  |
|  | 34. | LD | 0.11 | Burner 2 flame failure |  |
|  | 35. | OUT | 11.05 | Burner 2trip |  |
|  | 36. | LD | 1.00 | Burner 3 flame failure |  |
|  | 37. | OUT | 11.06 | Burner 3 trip |  |
|  | 38. | LD | 1.0.1 | Burner 4 flame failure |  |
|  | 39. | OUT | 11.07 | Burner 4 trip |  |
|  | 40. | LD | 0.10 | Burner 1 flame failure |  |
|  | 41. | AND | 0.11 | Burner 2 flame failure |  |
|  | 42. | AND | 1.00 | Burner 3 flame failure |  |
|  | 43. | AND | 1.01 | Burner 4 flame failure |  |

| 44. |  | OUT |  | 12.00 |  | All flame fail |
| --- | --- | --- | --- | --- | --- | --- |
| 45. |  | LD |  | 1.02 |  | OBTV 1 close |
| 46. |  | AND |  | 1.03 |  | OBTV 2close |
| 47. |  | AND |  | 1.04 |  | OBTV 3close |
| 48. |  | AND |  | 1.05 |  | OBTV 4 close |
| 49. |  | OUT |  | 12.01 |  | All OBTV close |
| 50. |  | LD |  | 1.06 |  | HOTV close |
| 51. |  | OUT |  | 12.02 |  | HOTV close |
| 52. |  | LD |  | 1.07 |  | IGTV close |
| .53. |  | OUT |  | 12.03 |  | IGTV close |
| 54. |  | LDNOT |  | 10.07 |  | Boiler trip |
| 55. |  | AND |  | 12.00 |  | All flame fail |
| 56. |  | AND |  | 12.01 |  | All OBTV close |
| 57. |  | AND |  | 12.02 |  | HOTV close |
| 58. |  | AND |  | 12.03 |  | IGTV close |
| 59. |  | OUT |  | 12.04 |  | Purge Ready Permit |
| 60. |  | LD |  | 1.08 |  | Purge Start command |
| 61. |  | ANDNOT |  | TIM001 |  |  |
| 62. |  | OUT |  | 12.05 |  | Purge start given |
| 63. |  | LD |  | 12.04 |  | Purge Ready Permit |
| 64. |  | AND |  | 12.05 |  | Purge start given |
| 65. |  | TIM |  | 001 1 |  |  |
| 66. | LD |  | TIM001 |  |  |  |
| 67. | OUT |  | 12.06 |  | Purge complete |  |
| 68. | LD |  | 1.09 |  | Ignition gas pressure not low |  |
| 69. | OUT |  | 12.07 |  | Ignition gas pressure not low |  |
| 70. | LD |  | 12.06 |  | Purge complete |  |
| 71. | AND |  | 12.07 |  | Ignition gas pressure not low |  |
| 72. | OUT |  | 13.00 |  | IGTV open permit |  |
| 73. | LD |  | 12.06 |  | Purge complete |  |
| 74. | ANDNOT |  | 11.03 |  | HOTV trip |  |
| 75. | OUT |  | 13.01 |  | " HOTV open ON |  |
| 76. | LD |  | 1.10 |  | Ignition ON |  |
| 77. | OUT |  | 13.02 |  | Ignition ON |  |
| 78. | LD |  | 1.11 |  | Oil manual valve open |  |
| 79. | OUT |  | 13.03 |  | Oil manual valve open |  |
| 80. | LD |  | 2.00 |  | Scavenging valve close |  |
| 8.1. | OUT |  | 13.04 |  | Scavenging valve close |  |
| 82. | LDNOT |  | 1.06 |  | HOTV close |  |
| 83. | AND |  | 12.06 |  | Purge complete |  |
| 84. | AND |  | 13.02 |  | Ignition ON |  |
| 85. | AND |  | 13.03 |  | Oil manual valve open |  |
| 86. | OUT |  | 13.05 |  | Out 1 |  |
| 87. | LD |  | 13.04 |  | Scavenging valve close |  |
| 88. | AND |  | 2.01 |  | Atomizing steam manual valve open |  |

89.

AND

2.02

Atomizing steam pressure not low

90.

AND

13.05

Out

91.

OUT

13.06

OBTV open permit

92.

LD

2.03

OBTV open Push Button
operated

93.

AND

13.06

OBTV open permit

94.

OUT

13.07

OBTV open PB pressed

95.

LD

13.06

OBTV open permit

96.

AND

2.04

Oil gun Engaged

97.

AND

13.07

OBTV open PB pressed

98.

OUT

14.00

ATV open command

99.

LD

2.05

ATV open feedback

100.

OUT

14.01

ATV opened

101.

LD

14.00

ATV open command

102.

AND

14.01

ATV opened

103.

ANDNOT

14.03

OBTV close command

104.

OUT

14.02

OBTV open command

105.

LD

14.02

OBTV open command

106.

TIM

002 5

107.

LD

TIM002

108.

AND

0.10

Burner 1 flame failure

109.

OUT

14.03

OBTV close command

LD

1.02

OBTV 1 close

111.

OUT

14.04

OBTV 1 close

| StepInstructionOperandComment1.LD0.01Turbine oil pressure very low2.OUT10.01Turbine oil pressure very low3.LD0.02Gear box oil pressure very low4.OUT10.02Gear box oil pressure very low5. 'LD0.03Oil temperature very high6.OUT10.03Oil temperature very high7.LD0.04Over speed8.OUT10.04Over speed9.LD0.01Turbine oil pressure very low10.OR0.02Gear box oil pressure very low11.OR0.03Oil temperature very high12.OR0.04Over speed13.OUT10.05Auxiliary turbine trip14.LD0.05Deaerator level very low.15.OUT10.06Deaerator level very low16.LD0.06Suction DP very high BOILER AUXILIARIES LOGIC MNEMONICS |  |  |  |
| --- | --- | --- | --- |
| 112. | LD | 13.02 | Ignition ON |
| 113. | AND | 14.04 | OBTV 1 close |
| 114. | OUT | 14.05 | Scavenging Valve open |

115.END(OOl)End

|  | 17. | OUT | 10.07 | Suction DP very high |  |
| --- | --- | --- | --- | --- | --- |
|  | 18. | LD * | 0.07 | Bearing temperature very high |  |
|  | 19. | OUT | 11.00 | Bearing temperature very high |  |
|  | 20. | LD | 0.08 | Lube oil pressure very low trip |  |
|  | 21. | OUT | 11.01 | Lube oil pressure very low trip |  |
|  | 22. | LD | 0.05 | Deaerator level very low |  |
|  | 23. | OR | 0.06 | Suction DP very high |  |
|  | 24. | OR | 0.07 | Bearing temperature very high |  |
|  | 25. | OR | 0.08 | Lube oil pressure very low trip |  |
|  | 26. | OUT | 11.02 | Boiler feed pump trip |  |
|  | 27. | LD | 0.09 | Deaerator level low |  |
|  | 28. | OUT | 11.03 | Alarm |  |
|  | 29. | LD | 0.10 | Deaerator level high |  |
|  | 30. | OUT | 11.04 | Alarm |  |
|  | 31. | LD | 0.11 | Deaerator level very high |  |
|  | 32. | OUT | 11.05 | Alarm |  |
|  | 33. | LD | 1.00 | Both turbo driven pumps are tripped |  |
|  | 34. | OUT | 11.06 | Boiler feed pump 3 start |  |
|  | 35. | LD | 1.01 | Any one turbo driven pump Tripped |  |
|  | 36. | OUT | 11.07 | Fuel oil pump start |  |
|  | 37. | LD | 1.02 | Turbo driven DM water pump is not running |  |
|  | 38. | OUT | 12.00 | DM water pump start |  |
|  | 39. | END(OOl) |  | End |  |

SCOPE OF THE PROJECT

Our project is Fully Automatic Boiler control System with PLC based on Burner management system. Burner management is the control of fuel burning equipment required on steam generator for safety of operation. In earlier days of burner management, it was carried out by field wiring of various devices in series and parallel to perform the required logic sequences and safety interlocks.

The burner management system provides proper sequencing of equipment during normal startup, operating and shutdown procedures. In addition it provides for a fuel trip during adverse boiler or burner operating conditions. This is accomplished through the use of programmable logics and various interlocks.

Boiler requires special treatment in their control because of the complexity of their numerable controllable parameters and control actions. The requirements for the reliable and efficient operation of the boilers coupled with those of steam consumers make the problem of boiler control sufficiently complicated.

The burner management system essentially provides automatic sequencing of operation of connected boiler during start up and it's shut down. It should also indicate the operator the existing states of various elements of fuel burning equipment. The system must initiate safe shutdown procedures as and when an unsafe operating condition is detected.

In the existing control systems, interlocks or protections for tripping the turbine are realized by means of electromagnetic relay based system. But it has many drawbacks. Since entire logics used are hardwired between different contacts of different relays their reliability is low. The probability of plant getting affected due to relay failure is also more. The relay wiring takes up more space and also makes troubleshooting difficult. If any change in logic is required it is very difficult to

implement, since lot of wiring will have to be changed physically. So in view of inherent of electromagnetic relay based system; our project is to replace the logic implementation using PLC's. PLCs are easy for maintenance and their lifetime is very long so that plant engineers could program easily and could survive the harsh industrial environment.

The boiler process is controlled by manually and also automatically. For the proper continuous operation, it require a periodic or a continuous examination of different conditions to be satisfied for the switching purpose. So a person has to be appointed just for monitoring the temperature and pressure and do the switching operations. This is a cumbersome duty and wastage of labors. These problems can be avoided by an automated switching operation using PLC. This will account to saving of annual energy consumption and reduction in labors.

By means of automatic combustion control it become easy to maintain a constant steam pressure and uniform furnace drought and supply of air or fuel can be regulated to meet the changes in steam demand, i.e. the boiler operation become more flexible.

The steam produced in boiler is nearly saturated. This steam should not be used in turbine because the dryness fraction of the steam leaving boiler will be low. This results in the presence of moisture which causes corrosion of combustion blades. To raise the temperature of steam super heater is used. It supplies steam at constant temperature at different loads. So superheated steam increases turbine efficiency.

The proper setting of arrangement of FD and ID fans improve proper burning of fuel and achieve higher efficiency.

CONCLUSION

The ladder logics developed in such a way that the entire BMS works automatically and safely. Before switching the burner to work, all the essential parameters are subjected to certain levels of tolerance. This means an indication of the current status of each and every parameter is known to the controller. Without tripping the boiler readily to each error, the error levels of each parameter is subdivided and indications like low, high etc. is provided so that it can be checked and cleared without tripping the boiler. .

A local control panel is mounted near to the burner from which an indication of the system is available. Start/stop switches, emergency shut down switch etc. and lamp indicating the low, high etc. conditions along with the trip indicators are provided on this local control panel. The whole system is wired from the pump to the control room using a junction box.

This project titled 'Fully Automated Burner Management System using PLCs' is a combination of software programming and hardware interface circuit designed for the automatic control of Boiler used in FACT. Our proposed system uses OMRON make Programmable Logic Controllers instead of Relays. The Techno economical analysis shows that with smooth and safe running of boiler they could meet the steam and power requirements of 900TPD ammonia plant in Udyogamandal division.

REFERENCES

www.boilercontrol.com www.burnermanagement.com www.fact.co.in 0MR0N PLC, Manual

ANNEXURE

PROGRAMMABLE LOGIC CONTROLLER

1.	INTRODUCTION

Sequencing has traditionally been realized with relay techniques. During 1970s PLC become more & more common and today sequencing is normally implemented in software instead of using relays.

PLCs are industrially hardened microcomputers (computer based) that perform discrete or continuous control functions in a variety of processing plant & factory environment. A PLC produces on/off voltage outputs & can actuate elements such as electric motors, solenoids, fans, heaters and light switches. They are vital parts of industrial automation equipment found in all kinds of industries.

The medium sized PLCs perform all the relay replacement functions expected of it but also aids many other functions such as counting, timing and complex mathematical operations, to its repertoire. Most medium sized PLCs perform PID, feed forward &other control functions as well. In addition medium sized and large scale PLCs now have data

high way capabilities and they function well in DCS environment.

2.	PLC ARCHITECTURE

It is a digital electronic device, which uses a programmable memory that co-ordinates i/p & o/p modules to control process. A PLC has following hardware components;

a.	I/P & O/P Modules

b.	Processor

c.	Power Supply

d.	Programming Devices

The relation between units is;

-:>   O-

whjt

HDBULE

CttiTPaT MQtXJlE

-o  o-

A

o-

sflVER

PLC architecture consists of following units;

Programming device

Power Supply

CPU

Memory

I/O System Modules

Solenoids, motor

Switches, push button

O/P Device

I/P

Device

3.	TYPES OF MEMORY

Processor memory has thousands of memory locations that store information as binary l's (ON) & O's (OFF). These are known as words or registers

2 types of PLC memory are;

Store memory: Stores information on the status of I/O devices, preassigned values of internal relays status & values for mathematical functions. User memory: Stores ladder logic programs.

4.	LADDER DIAGRAMS

Ladder diagrams are traditional methods of describing relay logic of control circuits. Many switches are produced today from solid-state gates, but electromechanical relays are still used in many applications. Relays remain a necessary interface between control electronics & powered devices & for describing combinational & sequential network. They are also a basis for writing programs for PLC.

A ladder diagram reflects   a connectional wiring diagram of the physical arrangement of various components (switches, relays, motors, valves etc.) & their interconnections.

Ladder Diagram Symbols

There are few basic ladder diagram symbols that are used to express the meaning & purpose of a control circuit. Some of symbols are given below;

Burner Management System	Project '08

t—nrii»iiwc« . n.^.    . m.—^"T-»i—»-«^M-r- mi ii	■

H h	H/h

(A)Normally Open Contact	(B) Normally Closed Contact

-o  o-

k.OR*.LL- OPEN MA*fL*U.r OPERATED

Nf_»«*U.r CLOSES MANUALLY DPES-s-TEE

r~\

STATDR.SELAY OS

sca_D«ie cdil

HEATING ELEMENT ft*

DvEK LOAD UEMcE

|     X00

o   o

SELECTOR SWITCH

In addition to the ladder diagrams, several other techniques are used to program PLCs.

- Statement lists

- Sequence flowchart

- Block diagrams

LADDER DIAGRAM INSTRUCTIONS

0

Sr«bdl

=?ocess load

ld

lu not

0

and

and

0

and mot

<us?d far input)

□r

a?

©

symbol

process load

notation le

li) not

0

luad mot

AND

(.used far input)

and

PARAMETERCONVENTIONAL CONTROLPLC CONTROLTools used for automationHard wiringSoftware programmingSpace requirementsLarge amount of space to house the relays and connecting wires .Compact systemsPower ConsumptionsHighLowInstallationInstallation process is very difficult. Each relay needs to be tested individually for proper functioningEasier process & controls can be programmed using ladder logic & tested in stimulated environmentMaintenanceRegular wear & tear of relay and hardware takes placeNo maintenanceFlexibilityNot very adaptable to changesAdaptable to changesReliabilityProne to mechanical fault & failureHighly reliableDiagnosing problemsVery difficult to diagnoseEasy to diagnose as software contain options for trouble shooting &diagnosing problems

5. CONVENTIONAL VERSUS PLC CONTROL

ADVANTAGES OF PLC Cost reduction

Ease of programming & reprogramming plant *♦* The programming language is very simple

High stability & minimal maintenance *♦* Small physical size

*♦* Ability to communicate with computer systems in the plant

- Moderate to low initial investment cost

- Rugged construction

- Modular design

- Flexibility in adapting to complex control strategies

- Improvement in operator/machine dynamics to Consolidate operations and reduced man power

- Increased Accuracy and speed in executing signal transmission

- Only digital signals are involved, hence P1D, A/D, D/A converters are not required.

OMRON CPM1A

PLC used for project work is OMRON CPMIA CPU-21. It has only limited program & communication capabilities. Technical descriptions of the PLC, digital input & output modules use described below.

Power Supplies

| DESCRIPTION | RATED VOLTAGE | OUTPUT CAPACITY | AUXILIARY SUPPLY | PART No: |
| --- | --- | --- | --- | --- |
| DC POWER SUPPLY | 24DC | 30W | N/A | CPMIA-PD026 |

I/PNO: OFI/PI/PCOMMONCONNECTORPARTTYPEINPUTSVOLTSCURRENTTYPETYPENo:DC1612V DC6 mASHAREDTERMINAL24VDCBLOCK

Input Modules

CPUs

| MEMORY CAPACITY | I/O CAPACITY | BUILT IN I/Ps | BUILT IN RS232C PORT | SUPPORTS INNER BOARDS | SUPPORTS CONTROLLER LINK | PART No: |
| --- | --- | --- | --- | --- | --- | --- |
| PROGRAM 3.2K WORDS | 256 PTS | 16 DC I/P | YES | NO | NO |  |

!0/PNO:MAX.MAX.COMMONCONNECTPART NO: 1'TYPEOFSWITCHSWITCHITYPEOR TYPEO/PsINGNGVOLTSCURRENTjCONTA1624V DC2.AINDEPENDETERM1NACPMIOC2CT16NT SHAREDL BLOCK22CPMIOC224

Output Modules

FEATURES

| 1. | One-piece construction |
| --- | --- |
| 2. | Extra i/o capacity |
| 3. | Input filter function |
| 4. | Low maintenance design |
| 5. | Input interrupts |
| 6. | Quick-response Inputs |
| 7. | Interval timer |
| 8. | High speed counter |
| 9. | Analog settling function |
| 10. | Host link communications |

| 1 NO:OF I/O | CPU UNIT |  |  |  |  |  |  | CPMIA EXPANSION I/O |  |  |  |  |  |  |  |  |  |  | POWER |  |  | MO |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TERMINAL | TERMI1 |  |  | NALS |  |  |  | UN | TTE |  | RMF |  | MALS |  |  |  |  |  | SUPPLY |  |  | DEL |  |  |  |
| S ON THE | I/P |  |  | O/P |  |  |  | 1/ | 0/ |  | 1/ |  | 0/ | 1/ |  |  | 0/ |  |  |  |  | NU |  |  |  |
| i CPU UNIT |  |  |  |  |  |  |  | P | P |  | P |  | P | P |  |  | P |  |  |  |  | MB |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ER |  |  |  |
| 10 | 6point |  |  | 4point |  |  |  | - | - |  | - |  | - | - |  |  | - |  | AC |  |  | CP |  |  |  |
|  | s |  |  | s |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MIA |  |  |  |
|  | 00000 |  |  | 01000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |  |
|  | to |  |  | to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10C |  |  |  |
|  | 00005 |  |  | 01003 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DR- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | A |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DC |  |  | CP |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MIA |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ^DR- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | D |  |  |  |
| 20 | 12poin |  |  | 8point |  |  |  |  |  |  |  |  |  |  |  |  |  |  | AC |  |  | CP |  |  |  |
|  | ts: |  |  | s |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MIA |  |  |  |
|  | 00000 |  |  | 01000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |  |
|  | to |  |  | to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10C |  |  |  |
|  | 00011 |  |  | 01007 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DR- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | A |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DC |  |  | CP |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MIA |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DR- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | D |  |  |  |
| 30 | 18poin |  |  | 12poin |  |  |  | 12 | 8p |  | 12 |  | 8p | 12 |  |  | 8p |  | AC |  |  | CP |  |  |  |
|  | ts: |  |  | "ts |  |  |  | po | oin |  | po |  | oin | po |  |  | oin |  |  |  |  | MIA |  |  |  |
|  | 00000 |  |  | :01000 |  |  |  | int | ts |  | int |  | ts | int |  |  | ts |  |  |  |  | - |  |  |  |
|  | to |  |  | to |  |  |  | s: | 01 |  | s: |  | 01 | s: |  |  | 01 |  |  |  |  | 10C |  |  |  |
|  | 00011 |  |  | 01007 |  |  |  | 00 | 20 |  | 00 |  | 30 | 00 |  |  | 40 |  |  |  |  | DR- |  |  |  |
|  | 00100 |  |  | 01100 |  |  |  | 20 | 0 |  | 30 |  | 0 | 40 |  |  | 0 |  |  |  |  | A |  |  |  |
|  | to |  |  | to |  |  |  | 0 | to |  | 0 |  | to | 0 |  |  | to |  | DC |  |  | CP |  |  |  |
|  | .001.05 |  |  | 01103 |  |  |  | to | 01 |  | to |  | 01 | to |  |  | 01 |  |  |  |  | MIA |  |  |  |
|  |  |  |  |  |  |  |  | 00 | 20 |  | 00 |  | 30 | 00 |  |  | 40 |  |  |  |  | - |  |  |  |
|  |  |  |  |  |  |  |  | 21 | 7 |  | 31 |  | 7 | 41 |  |  | 7 |  |  |  |  | 10C . |  |  |  |
|  |  |  |  |  |  |  |  | 1 ' |  |  | 1 |  |  | 1 |  |  |  |  |  |  |  | DR- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | D |  |  |  |
| ; 40 | 24poin |  |  | 16poin |  |  |  | 12 | 8p |  | 12 |  | 8p | 12 |  |  | 8p |  | AC |  |  | CP |  |  |  |
|  | ts:000 |  |  | ts:010 |  |  |  | po | oin |  | "po |  | oin | po |  |  | oin |  |  |  |  | MIA |  |  |  |
|  | 00 to |  |  | 00 to |  |  |  | int | ts |  | int |  | ts | int |  |  | ts |  |  |  |  | - |  |  |  |
|  | 00011 |  |  | 01007 |  |  |  | s: | 01 |  | s: |  | 01 | s: |  |  | 01 |  |  |  |  | 10C |  |  |  |
|  | 00100 |  |  | 01100 |  |  |  | 00 | 20 |  | 00 |  | 30 | 00 |  |  | 40 |  |  |  |  | DR- |  |  |  |
| SPECIFICATIONS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item |  |  |  |  |  | .10-point' 20-point 30-point 40-point I/O I/O I/O I/O |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Power supply voltage/ frequency |  | AC power supply |  |  |  | 100 to 240 VAC, 50/60 Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | DC power supply |  |  |  | 24 VDC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Operating voltage range |  | AC power supply |  |  |  | 85 to 264 VAC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | DC power supply |  |  |  | 20.4 to 26.4 VDC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Power consumption |  | AC power supply |  |  |  | 30 VAC max. |  |  |  |  |  |  |  |  | 60 VAC max. |  |  |  |  |  |  |  |  |  |  |
|  |  | DC power supply |  |  |  | (See below.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inrush current |  |  |  |  |  | 30 A max. |  |  |  |  |  |  |  |  | 60 A max. |  |  |  |  |  |  |  |  |  |  |
| External power supply (AC only) " |  | Power supply voltage |  |  |  | 24 VDC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Power supply output capacity |  |  |  | 200 mA |  |  |  |  |  |  |  |  | 300 mA |  |  |  |  |  |  |  |  |  |  |
| ' Insulation resistance |  |  |  |  |  | 20MDmin. at 500 VDC protective earth terminal |  |  |  |  |  |  |  |  | between the AC terminals and the |  |  |  |  |  |  |  |  |  |  |
| Dielectric strength |  |  |  |  |  | 2,300 VAC at 50/60 Hz for one minute with a leakage current of 10 mA max. between all the external AC terminals and the protective earth terminal |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| i Noise resistance |  |  |  |  |  | Conforms to IEC61000-4-4, 2 kV (power lines) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Vibration resistance |  |  |  |  |  | 10 to 57 Hz with an amplitude of 0.075 mm, and 57 to 150 Hz with an acceleration of 9.8 m/s2 in the X, Y, and Z directions for 80 minutes each (i.e. swept for ] 8 minutes, 10 times). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Shock resistance |  |  |  |  |  | 147 m/s2 in the X, Y and Z directions 3 times each |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ambient temperature (operating) |  |  |  |  |  | ODto 55DC . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item10-point 20-point 30-point 40-point I/O ! I/O I/O I/OControl methodStored program method1 I/O control methodCombination of the cyclic scan and immediate refresh \ processing methods.Programming languageLadder diagram ;¦ Instruction word1 step per instruction, 1 to 5 words per instructionTypes of instructionsBasic instructions14 types Special79 types, 139 instructions ; CHARACTERISTICS Ambient humidity (operating) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10% to 90% (no condensation) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ambient environment (operating) |  |  |  |  | With no corrosive gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ambient temperature (storage) |  |  |  |  | -20Dto 75DC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Terminal screw size |  |  |  |  | M3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Power supply holding time |  |  |  |  | 10 ms min. for AC models, and 2 ms min. for DC models |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Weight |  |  | AC model: 400 g max. DC model: 300 g max. |  |  |  | AC model: 500 g max. DC model: 400 g max. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | AC model: 600 g max. DC model: 500 g max. |
| AC model: 700 g max. DC model: 600 g max. |  |  | instructions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Instruction execution time |  |  | Basic instructions |  |  |  | 0.72 to 16.2 us |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Special instructions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MOV instruction = 16.3 us |
| Program capacity |  |  | 2,048 words |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Maximum I/O points |  |  | CPU only |  |  |  | 10 points (6 input/ 4 output points) |  |  |  |  | 20 points (12 input/ 8 output points) |  |  |  |  |  | 30 points (18 input/ 12 output points) |  |  | 40 points (24 input/ po s 16 output points) |  |  |  |  |
| 100 points (60 input/ j 40 output points) |  |  |  |  |  |  | With Expansion I/O Unit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ! Input bits90 points (54 input/ 36 output points) |  |  |  |  |  |  | 00000 to 009 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 (Words 0 to 9) |
| Output bits |  |  |  |  |  |  | 01000 to 01915 (Words 10 to 19) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Work bits (IR Area) |  |  |  |  |  |  | 512: IR 20000 to IR 23115 (IR 200 to IR 231) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Special bits (SR Area) |  |  |  |  |  |  | 384: SR 23200 to SR 25515 (SR 232 to SR 255) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temporary bits (TR Area) |  |  |  |  |  |  | 8: TR 0 to TR 7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Holding bits (HR Area) |  |  |  |  |  |  | 320: HR 0000 to HR 1915 (HR 00 to HR 19) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Auxiliary bits (AR Area) |  |  |  |  |  |  | 256: AR 0000 to AR 1515 (AR 00 to AR 15) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Link bits (LR Area) |  |  |  |  |  |  | 256: LR 0000 to LR 1515 (LR 00 to LR 15) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| [ Timers/Counters |  |  | 128:TIM/CNT 000 to 127 100-ms timer: TIM 000 to TIM 127 10-ms timer: TIM 000 to TIM 127 Decremental counter, reversible counter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Data memory |  |  | Read/Write |  |  |  | 1,024 words (DM 0000 to DM 1023) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Read only |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 512 words (DM 6144 to DM 6655) . |
| Interrupt processing: External interrupt |  |  |  |  |  |  | 2 points (Response 4 points (Response time of 0.3 ms time of 0.3 ms max.) max.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Memory protection |  |  |  |  |  |  | Maintains the contents of the HR, AR, Counter and Data Memory Areas. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Memory backup |  |  |  |  |  |  | Flash memory: User program, data memory (Read only) (Non-battery powered storage) Super capacitor: Data memory (Read/Write), holding bits, auxiliary memory bits, counter (20-day storage at an ambient temperature of 25°C) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| : Self-diagnostic function |  |  |  |  |  |  | . CPU error (watchdog timer), memory errors, I/O bus errors |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 Program check |

checked during operation)Pulse output1 point: 2 kHzHigh-speed counter1 point: Single phase at 5 kHz or two-phase at 2.5 kHz (linear counting method) Incremental mode: 0 to 65535 (16-bit) Decremental mode:-32767 to 32767 (16-bit) 1 point: Single phase at 5 kHz or two-phase at 2.5 kHz (linear counting method) Incremental mode: 0 to 65535 (16-bit) Decremental mode:-32767 to 32767 (16-bit)Quick-response inputsTogether with the external interrupt input (minimum pulse width of 0.2 ms)Input time constantCan be set at 1 ms, 2 ms, 4 ms, 8 ms, 16 ms, 32 ms, 64 ms, or 128 ms.Analog settings2 points: (0 to 200)

Note: Bits that are not used for the I/O bits can be used as work bits.

No END instruction programming errors (constantly