TRANSFORMER PRO TECTION USING NUMERICAL RELAY

INTRODUCTION

The aim of this project is to analyze and upgrade existing transformer protection system in BPCL Kochi Refinery. Transformers are static devices totally enclosed and generally oil immersed. Therefore, chances of faults occurring on them are very rare." However the consequences of even a rare fault may be very serious unless the transformer is quickly disconnected from the system. This necessitates providing adequate automatic protection for transformer against possible faults.

Small distribution transformers are usually connected to the supply system through series fuses instead of circuit breakers. Consequently, no automatic protective relay equipment is required. However, the probability of faults on power transformers is undoubtedly more and hence protection is absolutely necessary.

The transformer is major and very important equipment in power system. It requires highly reliable protective devices. The protective scheme depends on the size of the transformer. The rating of transformers used in transmission and distribution system range from a few kVA to several hundred MVA . For small transformers of medium size ■over current relays are used. For large transformers differential protection is recommended.

We analyzed and studied the existing transformer protection relays used in BPCL. [There different types of protection employ different types of relays.

With the technological advances being made in generation protection section, the [generator protection using new methods have gathered momentum. Here we have studied about functioning of transformer protection using numerical relays.

BPCL KOCHI REFINERY

AMBALAMUGAL, ERNAKULAM

BPCL Kochi Refinery, formerly known as Cochin Refineries Limited is a public sector enterprise which came into being as a result of a three party agreement among the Government of India, Philips Petroleum Company of the United States of America and the Duncan Brothers of Calcutta.

The formation agreement provided for the construction of a petroleum refinery in South India Petroleum and for continuing technical collaboration with Philips during a number of years. Government was to see to the marketing of all domestic products and exercise control over the company.

MILESTONES OF GROWTH

YEAR	DEVELOPMENT

*	1966	Unit commissioned with Crude Oil Refining capacity

of 2.5 MMPTA

*	1973	Capacity expanded from 2.5 to 3.3 MMPTA

*	1984	Capacity expanded from 3.3 to 4.5 MMPTA

*	1989	Aromatic production commenced

- 1990	Captive power plant (26.3 MW) commissioned

- 1994	Capacity expanded to 7.5 MMPTA

❖	1998	Steam turbine generator (17.8) commissioned

i

- 1999	DHDS commissioned

- 2000	Company renamed as Kochi Refineries Limited

Bharat Petroleum Corporation Ltd acquired the Govt's share in KRL in March 2001. With this KRL became a subsidiary of BPCL. In 2005 KRL modified its DHDS and FCCU unit to meet the EURO specifications. In 2006 KRL merged with BPCL and became a SBU viz. BPCL KR.

PRODUCTS OF BPCL

- Natural Rubber Modified Bitumen (Rubberized Bitumen) NRMB

- Liquefied Petroleum Gas & Kerosene for households and industrial uses

- Petrol & Diesel for automobiles

- Naphtha, the major raw material for fertilizer and petrochemical industries

- Benzene for manufacture of caprolactum, phenol, insecticides and other chemicals

- Furnace oil and low sulphur heavy stock for fuel in industries

- Aviation turbine fuel (ATF) for aircrafts

- Special boiling point spirit used as a solvent in tyre industry

- Toluene for the manufacture of solvents and insecticides, pharmaceuticals & paints

- MTO (Textile grade) and MTO (Paint grade) for use in textile and paint industiy

- Poly isobutene for the manufacture of lubricants

- Sulphur for use in fertilizer, sugar, chemical and tyre industry

CAPTIVE POWER PLANT (CPP)

A captive power plant of 26.3 MW was commissioned in 1991. An additional captive power plant of 17.8 MW was commissioned in 1998.

Captive Power Plant (CPP) is the heart of BPCL. It has a gas turbine generator (GTG) and a steam turbine generator (STG) which caters the electrical load of entire refinery. The captive power plant generates about 7 lakhs units of electrical energy on an average day in which the contribution of GTG is about 65% and STG about 30%. The remaining 5% is contributed by TG, which generates at 3.3KV level. BPCL also have 66KV feeders for KSEB substations, which are normally kept as emergency stand of source central maximum demand of 20 MVA. The 66KV feeder's line 1 and line 2 are tapped from (Kalamassery-Vyttila) No.l feeder and (Kalamassery-Vyttila) No.2 feeder respectively. The 66KV/11KV transformer TR-1 & TR-2 primary windings (66KV side) are kept energized always, synchronizing with state grid. This is done to draw power when required.

Power is distributed to plants through XLPE cables both buried underground and on GRP trays. Primary process substation, FCCU substation, CDUI substation, ACTP substation, PIBU substation, CPP offsite substation, Crude booster substation and P1BL substation receive 11KV supply directly from CPP. The electrical system & BPCL also consists of about 80 transformers.

66KV, 25/35MVA POWER TRANSFORMER

SPECIFICATIONS

| MVA |  | 25/35 |
| --- | --- | --- |
| Type of cooling |  | ONAN/ONAF |
| Voltaf | ie Ratio (no load) |  |

HV LV Phase

70KV 11KV

3

Normal Current

HV	206.2/288.7 Amps

LV	1312.1/1837.0 Amps

| Tap changer | OLTC (BHEL) |
| --- | --- |
| Frequency | 50Hz |
| Temperature rise | 50/55c |

Connections

HV	star

LV	delta

Insulation level

HV	325KVp/140KVrms

HVN	170KVp/75KVrms

LV	75KVp/28Kvrms

Make	GEC (tr 1), Volt amp (tr 2)

66KV CURRENT TRANSFORMER (CT)

SPECIFICATIONS

| Made to | BIS 2705/1981 |
| --- | --- |
| Max system voltage | 76.5KV |
| Rated STC | 25KA for 1 sec |
| Rated primary | 600/450/300 Amp |
| Secondary | 1 A/1A |
| Rated burden | Nil/30VA |
| Accuracy class | Core 1 PS |
| Min knee point volt | 800/1200V |
| Max RCT at 75C | 2.5/5ohms |
| Insulation level | 140/325KV |
| Frequency | 50Hz |
| Make | Automatic Electric Ltd |

66KV POTENTIAL TRANSFORMER

SPECIFICATIONS

| Made to | ISS 3156/1978 |
| --- | --- |
| Phase | One |
| Service Volt | 72.5KV |
| Frequency | 50Hz |
| Ratio | 66/root 3Kv |
| Core 1 | 110/root 3v |
| Core 2 | 110/root3v |
| Core 3 | 110/root3v |
| Burden Core 1 Core 2 Core 3 100VA 100VA 50VA Class 0.5 3P 3P 3P |  |
| Type | Earthed |
| Make | Automatic Electric Ltd |

NEED FOR PROTECTION

Protection is installed to detect the fault occurrences and to isolate the faulty equipments. So that the damage to the faulty equipment is limited and disruption of supplies to the adjacent unaffected equipment is minimized.

In a power system consisting of generators, motors, transformers etc. it is inevitable that sooner or later when a fault occurs it must be quickly detected and the faulty equipment must be disconnected from the system. If the faults are not detected quickly it causes unnecessary interruption of service to the customers.

Generally fuse performs the function of detection and interruption. But it is limited only to low voltage circuits. For high voltage circuits relays and circuit breakers are used.

So in brief: - Protection must detect faults and abnormal working conditions and ■isolates faulty equipments so as to limit damage caused by fault energy and to limit effect on rest of the system.

COMMON TRANSFORMER FAULTS

Transformer may suffer only from:

i.	Open circuit

ii.	Over heating

iii.	Winding short circuits (eg: earth- faults, phase to phase faults & inter-turn
faults)

Open circuit fault

An open circuit in one phase of a three-phase transformer may cause undesirable heating. In practice, relay protection is not provided against open circuits because this condition is relatively harmless. On the occurrence of such a fault, the transformer can be disconnected manually from the system

Over heating fault

Over heating of the transformer is usually caused by sustained overloads or short circuits & very occasionally by the failure of the cooling system. The relay protection is :also not provided against this contingency and thermal accessories are generally used to sound an alarm or control the banks of fans.

Winding short- circuit fault

Winding short-circuits (also called internal faults) on the transformer arise from deterioration of winding insulation due to over heating or mechanical injury. When an [internal fault occurs, the transformer must be disconnected quickly from the system [because a prolonged arc in the transformer may cause oil fire. Therefore, relay protection is absolutely necessary for internal faults.

PROTECTIVE RELAYS

"Protective relay is a device that detects the faults and initiates the operation of the circuit breaker to isolate the defective element from the rest of the system."

High-performance protective relaying comes into its own when it's a question of minimizing power system operating costs. Uncomplicated operation, convenient commissioning tools and flexible communication are all important elements when service and maintenance costs have to be reduced.

These relays not only handle fault detection and location tasks but also control, metering and monitoring functions. And it is these additional functions - impossible before the advent of numerical technology - which offer major cost-cutting potential.

The relays detect the abnormal conditions in the electric circuits by constantly measuring the electrical quantities which are different under normal and fault conditions. The electrical quantities which may change under fault conditions are voltage, current, frequency and phase angle. Through the changes in one or more of these quantities, the faults signal their presence, type and location to the protective relays. Having detected the fault, the relay operates to close the trip circuit of the breaker. This results in the opening iof breaker and disconnection of faulty circuit.

FUNDAMENTAL REQUIREMENS OF PROTECTIVE RELAYING

- Selectivity	i

- Speed

- Sensitivity	I

- Reliability

- Simplicity

- Economy

Protection relays can be classified in various ways depending on their construction, functions and are discussed below.

CLASSIFICAION OF PROTECTIVE RELAYS BASED ON TECHNOLOGY

Protective relays can be broadly classified into the following categories depending on the technology used for their construction and operation.

- Electromagnetic relays

- Static relays

- Microprocessor-based relays

Electromagnetic relays:' It includes attracted armature, moving coil and induction disc and induction cup type relays. Electromagnetic relays contain an electromagnet (or permanent magnet) and a moving part. When the actuating quantity exceeds a certain predetermined value, an operating torque is developed which is applied on the moving part. This causes the moving part to travel and to finally close a contact to energize the trip coil of the breaker.

Static relays:-

Static relays contains electronic circuits which may contain transistors, ICs, diodes and other electronic components. There is a comparator circuit in the relay, which compares two or more voltages and gives an output, which is applied to either a slave ■ready or a thyristor circuit. The slave ready is an electromagnetic relay which finally ;closes the contact. A static relay containing a slave ready is semi-static relay. A relay kising thyristor circuit is a wholly static relay. Static relay possess the advantage of having ilow burden on CT and PT, fast operation, absence of mechanical inertia and contact trouble, long life and less maintenance. Static relays have proved to be superior to electromagnetic relays and they are being used for the protection of important lines, power stations and substations. Yet they have not completely replaced electromagnetic relays. Static relays are treated as an addition to family of relays. Electromagnetic relays continue to be in use because of their simplicity and low cost. Their maintenance can be done by less qualified personal, where as the maintenance and repair of static relays requires personnel's trained in solid-state device.

Microprocessor-based protective relays;-

Microprocessor-based protective relays are the latest development in this area. With the development in VLSI Technology, Sophisticated and fast microprocessor are coming up. Their applications to the problems of protective relaying schemes are of current interests to power engineers. The inherit advantages of microprocessor-based relays over static relays with or a very limited range of applications, are attractive, flexibility due to their programmable approach. Microprocessor-based protective relays can provide protection at low cost and compete with conventional relays. The present downward trend in the cost of large-scale integrated circuit will encourage wide applications of microprocessor-based applications of microprocessor-based relays for the protection modem complex power network.

| TECHNOLOGY COMPARISON FOR PROTECTIVE RELAYS |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SI. No | SUBJECT |  | ELECTRO MECHANICAL |  | STATIC/ ELECTRONIC |  | NUMERICAL |  |
| 1 | Measuring elements/ Hardware |  | Induction disc, Electromagnets, Induction cup, Balance Beam |  | Discrete R, L, C Transistors, Analogue ICs comparators |  | Microprocessor s, Digital ICs, Digital signal processors |  |
| 2 | Measuring method |  | Electrical Qtys converted into mechanical force, torque |  | Level detectors, comparison with reference value in analogue comparator |  | A/D conversion, Numerical algorithm techniques evaluate trip criteria |  |
|  | Timing function |  | Mechanical clock works, dashpot |  | Static timers |  | Counters |  |
| 4 | Sequence of events |  | Not possible |  | Not possible |  | Provided |  |
| 5 | Visual indication |  | Flags, targets |  | LEDs |  | LEDs, LCD Display |  |
| 6 | Trip command |  | Additional trip duty relay required |  | Additional trip duty relay required |  | Trip ■ duty contact inbuilt |  |
| 7 | Construction size |  | Bulky |  | Modular, compact |  | Most compact |  |
| 8 | Self monitoring |  | No |  | Yes • Hardware Partly • Power supply |  | Yes • Hardwar e • Power supply • O/P relays • Firm ware CT, PT ckts |  |
| 9 | Temp. Stability |  | Yes |  | No |  | Yes |  |
| 10 | Vibration proof |  | No |  | Yes |  | Yes |  |
| 11 | Contacts |  | Fixed |  | Fixed |  | Freely |  |
|  |  | assignments |  |  |  |  |  | marshable |
| 12 |  | Parameter setting |  | *Plug setting, dial setting |  | Thumb wheel, potentiometers, dual in line switches |  | Keypad for numeric values, through computer/ laptop |
| 13 |  | Binary inputs for adaptive relaying |  | Not available |  | Not available |  | Freely marshable from 24V to 250V |
| 14 |  | CT loading/' Burden |  | 8 to 10 VA |  | 1 VA |  | < 0.5 VA |
| 15 |  | CT offset adjustment |  | No |  | No |  | Yes |
| 16 |  | Harmonic immunity |  | No |  | Possible through analogue fdtering |  | Yes, digital fdtering incorporated |
| 17 |  | Calibration |  | Frequently required as settings drift due to aging |  | Frequently required as settings drift due to aging |  | Not required as setting are stopped in memory in digital forma T |
| 18 |  | Auxiliary supply |  | Required |  | Required |  | Required |
| 19 |  | Electromagnetic/ electrostatic/ high frequency disturbances |  | Immune |  | Susceptible |  | Immune |
| 20 |  | Multiple characteristic |  | Not possible |  | Not possible |  | Possible |
| 21 |  | Integrated protective functions |  | Not possible |  | Not possible |  | Possible |
| ■22 |  | Range of settings |  | Limited |  | Wide |  | Wide |
| 23 |  | Operational value indication |  | Not possible |  | Possible |  | Possible |

| 24 | 'Fault disturbance recording | Not possible | Not possible | Possible |
| --- | --- | --- | --- | --- |
| 25 | Digital communication port | Not possible | Not available | Available |
| 26 | Commissioning support from relay | No | No | Yes |

VARIOUS PROTECTION SCHEMES

PERCENTAGE DIFFERENTIAL PROTECTION

Percentage differential protection is used for the protection of large power transformers having ratings of 5MVA and above. This scheme is employed for the protection of transformers against internal short circuits. It is not capable of detecting incipient faults. Figure shows schematic diagram of percentage differential protection for a Y-A transformer. The direction of current and the polarity of the CT voltage shown in fig are for s particular instant. The convention for making the polarity for upper and lower CT is the same. The current entering end has been marked as positive. The end at which current is leaving has been marked negative.

CT

Secondare

Primary

Relay Coils

7

The connections are made in such a way that under normal conditions or in case of external faults the current flowing in the operating coil of the relay due to CTs of the primary side is in opposition to the current flowing due to the CTs of secondary side. Consequently, the relay does not operate under such conditions. If a fault occurs on the winding, the polarity of the induced voltage of the CT of the secondary side is reversed. Now the currents in the operating coil from CTs of both primary and secondary side are in the same direction and cause the operation of the relay. To supply the matching current in the operating winding of the relay, the CT which are on the star side of the transformer are connected in delta. The CTs which are on the delta side of the transformer are connected in star. In case of Y- A connected transformer there is a phase shift of 30 degree in line currents. Also the above mentioned CTs connections also correct this phase shift. Moreover, zero sequence current flowing on the star side of the transformers does not produce current outside the delta on the other side. Therefore, the zero sequence ;current should be eliminated from the star side. This condition is also fulfilled by CTs in delta on the star side of the transformer.

In case of star/star connected transformer CTs on both sides should be connected [in delta. In case of star/star connected transformer, if star point is not earthed, CTs may [be connected in star on both sides. If the star point is earthed and CTs are connected in [star, the relay will also operate for external faults. Therefore, it is better to follow the rule

that CTs associated with star connected transformer windings should be connected in I delta and those associated with delta windings in star.

The relay settings for transformer protection are kept higher than those for [alternators. The typical value of alternator is 10% for operating coil and 5% for bias. The corresponding values for transformer may be 40% and 10% respectively. The reasons for a higher setting in the case of transformer protection are, 1. A transformer is provided with on-load tap changing gear. The CT ratio cannot be changed with varying transformation ratio of the power transformer. The CT ratio

is fixed and it is kept to suit the nominal ratio of the power transformer. Therefore, for taps other than nominal, an out of balance current flows through the operating coil of the relay during load and external fault conditions. 2. When a transformer is on no-load, there is no-load current in the relay. Therefore, its setting should be greater than no-load current.

OVERHEATING PROTECTION

The rating of a transformer depends on the temperature rise above an assumed maximum ambient temperature. Sustained overload is not allowed if the ambient temperature is equal to the assumed ambient temperature. At lower ambient temperature some over loading is permissible. The over loading will depend on the ambient temperature prevailing at the time of operation. The maximum safe over loading is that it does not over heat the winding. The maximum allowed temperature is about 95 degree Celsius. Thus the protection against over load depends on the winding temperature which is usually measured by thermal image technique.

In the thermal image technique, the temperature sensing device is placed in the transformer oil near the top of the transformer tank. A CT is employed on LV side to supply current to a small heater. Both the temperature sensing device and the heater are

placed in a small pocket. The heater produces a local temperature rise similar to that of the main winding. The temperature of the sensing element is similar to that of the [winding under all conditions. In a typical modern system the heat sensitive element is a [silicon resistor or silistor. It is incorporated with the heating element and kept in a [thermal moulded material. The whole unit forms a thermal replica of the transformer Ivinding. It is in the shape of a small cylinder and is placed in the pocket in the transformer tank about 25cm below the tank top, which is supposed to be the hottest layer [in the oil. The silistor is used as an arm of a resistance bridge supplied from a stabilized fc)C source. An indicating instrument is energized from the out of balance voltage of the bridge. Also the voltage across the silistor is applied to a static control circuit which controls cooling pumps and fans, gives warning of over heating, and ultimately trips the transformer circuit breaker.

OIL PRESSURE RELIEF DEVICES

An oil pressure relief device is fitted at the top of the transformer tank. In its simplest form, it is a frangible disc located at the end of a relief pipe protruding from the top of the transformer tank. In case of a serious fault, a surge in the oil is developed, which bursts the disc, thereby allowing the oil to discharge rapidly. This avoids the explosive rapture of the tank and the risk of lire.

The drawback of the frangible disc is that the oil which remains in the tank after rupture is left exposed to the atmosphere. This drawback can be overcome by employing a more effective device: a spring controlled pressure relief valve. It operates when the pressure exceeds 10 psi but closes automatically when the pressure falls below the critical level. The discharged oil can be ducted to a catchments pit where random discharge of oil is to be avoided. The device is commonly employed for large power transformers of the rating 2MVA and above but it can also be used for distribution transformers of 200kVA and above.

OVERFLUXING PROTECTION

The magnetic flux increases when voltage increases. This results, in increased iron [loss and magnetizing current. The core and core bolts get heated and the lamination [insulation is affected. Protection against over fluxing is required where over fluxing due [to sustained over voltage can occur. The reduction in frequency also increases the flux [density and consequently it has similar affects as those due to over voltage. The expression of flux in a transformer is given by

<j> =kE/f

Where <j)=flux, f= frequency, E=applied voltage and k=constant

Therefore, to control flux, the ratio E/f is controlled. When E/f exceeds unity, it has to be detected. Electronic circuits with suitable relays are available to measure the E/f ratio. Usually 10% of over fluxing can allowed without damage. If E/f exceeds 1.1 overfluxing protections operates. Overfluxing does not require high speed tripping and hence instantaneous operation is undesirable when momentary disturbance occur. But the transformer should be isolated in one or two minutes at the most if overfluxing persists.

BUCHHOLZ RELAY

Buchholz relay is gas-actuated relay installed in oil-immersed transformer for protection against all kind of faults. It is used to give alarm in case of slow-developing faults in transformer and to disconnect from the supply in event of severe internal faults. It is usually installed in the pipe connecting the conservator to the main tank as shown in fig. It is a universal practice to use Buchholz relays on all such oil-immersed transformers having rating in excess of 750kVA.

\

K

Transformer main tank

OPERATION

The operation is as follows.

- In case of incipient faults within the transformers, the heat due to fault causes the decomposition of some transformer oil in the main tank. The product of decomposition contains more than 75% of Hydrogen gas. The Hydrogen gas being light tries to go into the conservative and in the process gets entrapped in the upper part of relay chamber. When a predetermined amount of gas gets accumulated, it exerts sufficient pressure on the float to cause it to tilt and close contacts of Mercury switch attached to it. This completes the alarm circuits to sound an alarm.

- If serious faults occur in the transformer, an enormous amount of gas is generated in the main tank. The oil in the main tank rushes towards the conservator via the Buchholz relay and in doing so tilts to close the contacts of Mercury switch. This completes the trip circuit to open the circuit breaker controlling the transformer.

ADVANTAGES

- It is the simplest form of transformer protection.

- It detects the incipient faults at a stage much earlier than is possible with other forms of protection.

DISADVANTAGES

- It can only be the used with oil immersed transformer equipped with conservator tanks.

- The device can detect only faults below oil level in the transformer. Therefore, separate protection is needed for connecting cables.

EARTH-FAULT OR LEAKAGE PROTECTION

An earth-fault usually involves a partial a partial breakdown of winding insulator jto earth. The resulting leakage current is considerably less than the short circuit current. [The earth-fault may continue for a long time and cause considerable damage before if ultimately develops into a short circuit and removed from the system under these circumstances, it is profitable to employ earth fault relay is essentially an over current relay of low setting and operates as soon as an earth-fault or leak develops.

Restricted earth fault protection

Restricted earth fault protection as shown in the fig provides better protection. This scheme is used for the winding of the transformer connected in star where the |neutral point is either solidly earthed or earthed through impedance. The relay used is of high impedance type to meet the scheme stable for external fault

' supply

7^

:ffj1n_

Ml

load

Residual oveiciuient Relay

Res tiic fe A E ai th fault Relay

The residual over current relay operates only for ground fault in the transformer. The differential protection is supplemented by restricted earth fault protection in case of transformer with its neutral grounded through resistance. For such a case only about 40% of the winding is protected with a differential relay pick up setting as low as 20% of the CT winding.

OVERCURRENT RELAYS

Over current relays are used for the protection of transformers of rating lOOkVA *and below 5MVA. An earth fault tripping element is also provided in addition to the over (current feature. Such relays are used as primary protection for transformers which are not (provided with differential protection. Over current relays are also used as back-up protection where differential protection is used as primary protection.

For small transformers, over current relays are used for both overload and fault [protection. An extremely inverse relay is desirable for overload and light faults, with [instantaneous over current relay for heavy faults. A very inverse residual current relay with instantaneous relay is suitable for ground faults.

TIME-CURRENT CHARACTERISTICS

A wide variety of time-current characteristics is available for over current relays. [The name assigned to an over current relay indicates its time-current characteristics as [described below

DEFINITE TIME OVER CURRENT RELAY:-

It operates after a predetermined time when the current exceeds its pick up value. [The operating time is constant, irrespective of the magnitude of the current above the pick up value. The desired definite operating time can be set with the help of an [intentional time delay mechanism provided in the relaying unit.

The residual over current relay operates only for ground fault in the transformer. The differential protection is supplemented by restricted earth fault protection in case of transformer with its neutral grounded through resistance. For such a case only about 40% of the winding is protected with a differential relay pick up setting as low as 20% of the CT winding.

OVERCURRENT RELAYS

Over current relays are used for the protection of transformers of rating 100kVA and below 5MVA. An earth fault tripping element is also provided in addition to the over current feature. Such relays are used as primary protection for transformers which are not provided with differential protection. Over current relays are also used as back-up protection where differential protection is used as primary protection.

For small transformers, over current relays are used for both overload and fault protection. An extremely inverse relay is desirable for overload and light faults, with instantaneous over current relay for heavy faults. A very inverse residual current relay with instantaneous relay is suitable for ground faults.

TIME-CURRENT CHARACTERISTICS

A wide variety of time-current characteristics is available for over current relays. The name assigned to an over current relay indicates its time-current characteristics as [described below

DEFINITE TIME OVER CURRENT RELAY:-

It operates after a predetermined time when the current exceeds its pick up value.
The operating time is constant, irrespective of the magnitude of the current above the
pick up value. The desired definite operating time can be set with the help of an
Intentional time delay mechanism provided in the relaying unit.	,

INSTANTANEOUS OVER CURRENT RELAY:-

It operates in definite time when the current exceeds its pick up value. The operating time is constant, irrespective of the magnitude of the current. There is no intentional time delay. It operates in zero seconds or less.

Sometime a term like "high set" or "high speed" is used for very fast relays having operating times less than 0.1 sec.

INVERSE TIME OVER CURRENT RELAY:-

It operates when the current exceeds its pick up value. The operating point depends upon the magnitude of the operating current. The operating time decreases as the current increases.

INVERSE DEFINITE MINIMUM TIME (IDMT) LAG RELAY:-

In these relays the time of operation is approximately inversely proportional to the smaller values of current or other quantity causing operation and tends to be definite minimum time as the value increases without limit.

DEFINITION & BLOCK DIAGRAM OF NUMERICAL RELAY

Numerical relays are those in which measured ac quantities are sequentially converted into numeric data form. A microprocessor performs mathematical and/or operation on the data to make decision. In numerical relay there is an additional entity, the software, which runs in the background and which actually run in the relay. With the advent of numerical relay the emphasis has shifted from hardware to software. What distinguishes numerical relay from the other is software.

Multiple xei

st fiit	-TS'T^N

toveision      ;

command      jMiaopioce | hip

sso:

Analogue to

jligit.il

conveiter

End of reversion

Figure shows the block diagram of a numerical relay. The signals from the CTs and PTs cannot be sampled directly and converted to the digital form. This is to make sure that the signal does not contain frequency components having a frequency greater than one half of the sampling frequency. This limit is enforced by the sampling theorem. Therefore, the signals are first passed through a low-pass filter, which has to be an analogue type of filter because digital pressing can only take place after the frequency spectrum of the signal is properly shaped.

Next the analogue signal is sampled and held constant during the time the value is converted to digital form. The sample and hold circuit is an absolute must.

The sampled and hold value is passed on to the ADC through a multiplier so as to accommodate a large number of input signals. The sample and hold circuit and the ADC work under the control of the microprocessor and communicate with it with the help of control signal such as the end-of -conversion signals issued by the ADC. The ADC-passes on the digital representation of the instantaneous value of the signal to the microprocessor via as input port. The output ports of the ADC may be 4, 8, 12, 16, Or 32 bits wide or even wider. The wider the output of the ADC, the greater its resolution.

The incoming digital values from the ADC are stored in the RAM of the microprocessor and processed by the relay software in accordance with an underlying relaying algorithm. The microprocessor issues the trip signal on one of the bits of its output port which is then suitably processed so as to make it compatible with the trip coil of the CB. The microprocessor can also be used to communicate with other relays or another supervisory computer, if so desired. The relaying program or the relay software, which resides in the EPROM, can only be upgraded or modified by authorized personnel. Thus new features and functionalities can be added to an existing relay by upgrading its software.

A numerical relay can be made to run a program which periodically performs a self diagnostic test and issues an alarm signal if any discrepancy is noticed. Other features like a watch-doze timer can also be implemented, which issues an alarm if the [microprocessor does not reset it, periodically within a stipulated time and a few milliseconds. This gives an increased user confidence and improves the reliability and the relay.

Relay Setting Types

The relay requires three types of settings. The settings, described below, determine how the relay recognizes and responds to adverse operating conditions to protect your power apparatus equipment. Each relay is delivered with a set of parameters that are preprogrammed at the factory.

System settings inform the relay what it is protecting (transformer or generator/motor) and provide system information such as CT ratios and MVA ratings. The relay's differential protection function and overload function use this information to compute the system's protection requirements.

Protection settings, such as the differential current pickup and thermal overload condition, are also required. The protection functions must be set either to operate and automatically trip (ON), to operate but not trip (BLOCKED), or to not operate (OFF).

Relay configuration settings tell the relay how to process the input information land to logically associate it with the output devices. If desired, you can reassign the [binary inputs, annunciations, and the function of the relay's output signals, trip relays, [and LEDs. Configuration also is referred to in this manual as programming or marshalling the relay.

Each relay input and output setting is assigned to an address number that you [must access to display or to change the setting. Address numbers are grouped typically in blocks according to their function.

7UT61 SERIES NUMERICAL RELAY

The numerical differential protection 7UT61 is a fast and selective short-circuit protection for transformers of all voltage levels, for rotating machines, for series and ^shunt reactors, or for short lines and mini-bus bars.

Two models are available. They are

- 7UT612

- 7UT613

7UT612 NUMERICAL RELAY

The SIPROTEC 7UT612 differential protection relay is used for fast and selective fault clearing of short-circuits in two winding transformers of all voltage levels and also in rotating electric machines like motors and generators, for short two terminal lines and busbars up to 7 feeders.

The specific application can be chosen by parameterization. In this way an optimal adaption of the relay to the protected object can be achieved

In addition to the differential function a backup over current protection for 1 winding / star point is integrated in the relay. Optionally, a low or high-impedance restricted earth-fault protection, a negative sequence protection and a breaker failure protection can be used. With external temperature monitoring boxes (RTD-boxes) a maximum of 12 temperatures can be measured and supervised in the relay. Therefore, complete thermal supervision of a transformer is possible.

The protection relay can be parameterized for use with three-phase and single-phase transformers. In addition to this, a thermal replica is integrated for the supervision of the ohmic losses in the plant.

FUNCTION OVERVIEW

- Differential protection for 2 winding transformers (3-/1-phase)

- Differential protection for motors and generators

- Differential protection for short two terminal lines

- Differential protection for busbars up to 7 feeders (phase-segregated or with summation CT)

PROTECTION FUNCTIONS

- Differential protection with phase-segregated measurement

- Sensitive measuring stage for low-fault currents

- Restraint against inrush of transformer

- Phase-/earth overcurrent protection

[ ♦	Overload protection with or without temperature measurement

t ♦	Negative-sequence protection

♦	Breaker failure protection

- Low-or high-impedance restricted earth fault (REF)

- Over excitation protection

4  Thermal monitoring of transformer via temperature measurement with external thermo-box up to 12 measuring points

CONTROL FUNCTIONS

♦	Commands for. Ctrl, of CB and isolators

MONITORING FUNCTIONS

- Self-supervision of the relay

- Trip circuit supervision

- Oscillographic fault recording

- Permanent differential and restraint current measurement

COMMUNICATION INTERFACES

- PC front port for setting with DIGSI 4

- System interface protocols -IEC 60870-5-103

- PROFIBUS-FMS/-DP

- MODBUS

- DNP 3.0

- Service interface for DIGSI 4 (modem)/temperature monitoring (thermo-box)

- Time synchronization via IRIG-B/DCF 77

7UT613 NUMERICAL RELAY

The SIPROTEC 7UT613 differential protection relays are used for fast and selective fauld clearing of short-circuits in transformers of allj voltage levels and also in rotating electric^ machines like motors and generators, for short lines and bus bars.

The specific application can be chosen by parameterization.   In  this  way  an  optimal adaptation of the relay to the protected object can be achieved.

In addition to the differential function, a backup overcurrent protection for 1 winding/ star point is integrated in the relay. Optionally, a low or high-impedance restricted earth-fault protection, a negative-sequence protection and a breaker failure protection can be used. With external temperature monitoring boxes a maximum of 12 temperatures can be measured and monitored in the relay. Therefore, complete thermal monitoring of a transformer is possible, e.g. hot-spot calculation of the oil temperature.

The protection relay can be parameterized for use with three-phase and single-phase transformers.

The integrated programmable logic (CFC) allows the users to implement their iown functions, e.g. for the automation of switchgear (interlocking). User-defined messages can be generated as well. The flexible communication interfaces are open for Imodem communication architectures with control system. Alternatively to the conventional overload protection, the relay can also provide a hot spot calculation acc. to J1EC60435

FUNCTION OVERVIEW

- Differential protection for 2 or 3 winding transformers (3-/1-phase)

- Differential protection for motors and generators

- Differential protection for short 2 up to 3 terminal lines

- Differential protection for busbars up to 9 feeders (phase-segregated or with summation CT)

PROTECTION FUNCTIONS

♦	Differential protection with phase-segregated measurement
4	Sensitive measuring stage for low-fault currents

- Fast tripping for high-fault currents

- Restraint against inrush of transformer

- Phase-/earth overcurrent protection

- Overload protection with or without temperature measurement

- Negative-sequence protection

- Breaker failure protection

- Low-or high-impedance restricted earth fault (REF)

OVER EXCITATION PROTECTION

♦	Thermal monitoring of transformer via temperature measurement with external thermo-box up to 12 measuring points

CONTROL FUNCTIONS

- Commands for. Ctrl, of CB and isolators

- Control via keyboard, binary inputs, DIGSI 4 or SCADA system

- User-defined logic with CFC

MONITORING FUNCTIONS

- Self-supervision of the relay

- Extensive number of operational values (I, V, P, f, coscj) etc.)

- Trip circuit supervision

- Oscillographic fault recording

- Permanent differential and restraint current measurement

COMMUNICATION INTERFACES

- PC front port for setting with DIGSI 4

- System interface protocols

- IEC 60870-5-103

- PROFIBUS-FMS/-DP -MODBUS

- DNP 3.0

- Service interface for DIGSI 4 (modem)/temperature monitoring (thermo-box)

- Time synchronization via IRIG-B/DCF 77

Overall Operation

The numerical differential protection device SIPROTEC® 7UT612 is equipped with a powerful microcomputer system. This provides fully numerical processing of all functions in the device, from the acquisition of the measured values up to the output of commands to the circuit breakers. Figure 1-1 shows the basic structure of the device.

II

Figure 1-1     Hardware structure of the numerical differential protection 7UT612 —example for a two-winding transformer with sides S1 and S2

1

■ERROR

44-RUN

0

rj

to-	i

LEDs	I

on hi front I     panel, user-programmable

Output relays I user-programmable '

Display on the front panel

I    Front serial    i

operating interface * |

•LioPC

Time synchronization

1 radio

1 clock

Rear ssrial service interface

PC/modem/ thermobox

to

' SCADA

Serial system interface

Analog Inputs

The measuring inputs "MI" transform the currents derived from the instrument transformers and match them to the internal signal levels for processing in the device. The device includes 8 current inputs. Three current inputs are provided for the input of the phase currents at each end of the protected zone, a further measuring input (I7) may be used for any desired current, e.g. the earth current measured between the starpoint of a transformer winding and ground. The input Ig is designed for highly sensitive current detection thus allowing, for example, the detection of small tank leakage currents of power transformers or reactors, or — with an external series resistor — processing of a voltage (e.g. for high impedance unit protection). The analog signals are then routed to the input amplifier group "IA". The input amplifier group "IA" ensures a high impedance termination for the measured signals. It contains filters which are optimized in terms of band width and speed with regard to the signal processing. The analog/digital converter group "AD" has a multiplexer, analog/digital converters and memory modules for the data transfer to the microcomputer system "pC".

Microcomputer System

Apart from processing the measured values, the microcomputer system "pC" also executes the actual protection and control functions. In particular, the following are included:

- Filtering and conditioning of measured signals.

- Continuous supervision of measured signals.

- Monitoring of the pickup conditions of each protection function.

- Conditioning of the measured signals, i.e. conversion of currents according to the connection group of the protected transformer (when used for transformer differential   protection) and matching of the current amplitudes.

- Formation of the differential and restraint quantities.

- Frequency analysis of the phase currents and restraint quantities.

- Calculation of the RMS-values of the currents for thermal replica and scanning of the temperature rise of the protected object.

- Interrogation of threshold values and time sequences.

- Processing of signals for the logic functions.

- Reaching trip command decisions.

- Storage of fault messages, fault annunciations as well as oscillographic fault data for system fault analysis.

- Operating system and related function management such as e.g. data recording, real time clock, communication, interfaces etc.

- The information is provided via output amplifier "OA".

Binary Inputs and Outputs

The microcomputer system obtains external information through binary inputs such as remote resetting or blocking commands for protective elements. The "pC" issues information to external equipment via the output contacts. These outputs include, in ■particular, trip commands to circuit breakers and signals for remote annunciation of important events and conditions.

Front Elements

Light-emitting diodes (LEDs) and a display screen (LCD) on the front panel provide information such as targets, measured values, messages related to events or faults, status, and functional status of the 7UT612. Integrated control and numeric keys in conjunction with the LCD facilitate local interaction with the 7UT612. All information of jthe device can be accessed using the integrated control and numeric keys. The. information includes protective and control settings, operating and fault messages, and measured values (see also SIPROTEC® System Manual, order-no. E50417-H1176-C151). If the device incorporates switchgear control functions, the control of circuit ibreakers and other equipment is possible from the 7UT612 front panel.

Serial Interfaces

A serial operating interface on the front panel is provided for local communications with the 7UT612 through a personal computer. Convenient operation of all functions of the device is possible using the SIPROTEC® 4 operating program DIGSI® 4. A separate serial service interface is provided for remote communications via a modem, or local communications via a substation master computer that is permanently connected to the 7UT612. DIGSI® 4 is required. All 7UT612 data can be transferred to a central master or main control system through the serial system (SCADA) interface. Various protocols and physical arrangements are available for this interface to suit the particular application. Another interface is provided for the time synchronization of the internal clock via external synchronization sources. Via additional interface modules further communication protocols may be created. The service interface may be used, alternatively, for connection of a thermobox in order to process external temperatures, e.g. in overload protection.

Power Supply

The 7UT612 can be supplied with any of the common power supply voltages. Transient dips of the supply voltage which may occur during short-circuit in the power supply system, are bridged by a capacitor.

Applications

The numerical differential protection 7UT612 is a fast and selective short-circuit protection for transformers of all voltage levels, for rotating machines, for series and shunt reactors, or for short lines and mini-busbars with two feeders.

It can also be used as a single-phase protection for busbars with up to seven feeders. The individual application can be configured, which ensures optimum matching to the protected object.

The device is also suited for two-phase connection for use in systems with 162/3 Hz rated frequency.

A major advantage of the differential protection principle is the instantaneous tripping in the event of a short-circuit at any point within the entire protected zone. The current transformers limit the protected zone at the ends towards the network. This rigid limit is the reason why the differential protection scheme shows such an ideal selectivity.

For use as transformer protection, the device is normally connected to the current transformer sets at the higher voltage side and the lower voltage side of the power transformer. The phase displacement and the interlinkage of the currents due to the winding connection of the transformer is matched in the device by calculation algorithms. The earthing conditions of the star point(s) can be adapted to the user's requirements and are automatically considered in the matching algorithms.

For use as generator or motor protection, the current in the starpoint leads of the machine and at its terminals are compared. Similar applies for series reactors. Short lines tor mini-busbars with two feeders can be protected either. "Short" means that the [connections from the CTs to the device do not cause an impermissible burden for the current transformers.

Project Report '07
	1

For transformers, generators, motors, or shunt reactors with earthed starpoint, the current between the starpoint and earth can be measured and used for highly sensitive earth fault protection. The seven measured current inputs of the device allow for a single-phase protection for busbars with up to seven feeders. One 7UT612 is used per phase in this case. Alternatively, (external) summation transformers can be installed in order to allow a busbar protection for up to seven feeders with one single 7UT612 relay. An additional current input 18 is designed for very high sensitivity. This may be used e.g. for detection of small leakage currents between the tank of transformers or reactors and earth thus recognizing even high-resistance faults.

For transformers (including auto-transformers), generators, and shunt reactors, a high-impedance unit protection system can be formed using 7UT612. In this case, the currents of all current transformers (of equal design) at the ends of the protected zone feed a common (external) high-ohmic resistor the current of which is measured using the high-sensitive current input 18 of 7UT612.

The device provides backup time overcurrent protection functions for all types of protected objects. The functions can be enabled for any side. A thermal overload protection is available for any type of machine. This can be complemented by the evaluation of the hot-spot temperature and ageing rate, using an external thermobox to allow for the inclusion of the oil temperature. An unbalanced load protection enables the detection of unsymmetrical currents. Phase failures and unbalanced loads which are especially dangerous for rotating machines can thus be detected.

A version for 162/3 Hz two-phase application is available for traction supply (transformers or generators) which provides all functions suited for this application (differential protection, restricted earth fault protection, overcurrent protection, overload protection).A circuit breaker failure protection checks the reaction of one circuit breaker after a trip command. It can be assigned to any of the sides of the protected object.

Features

*t* Powerful 32-bit microprocessor system

♦J*. Complete numerical processing of measured values and control, from sampling and digitizing of the analog input values up to tripping commands to the circuit breakers.

♦>. Complete galvanic and reliable separation between internal processing circuits of the 7UT612 and external measurement, control, and power supply circuits because of the design of the analog input transducers, binary inputs and outputs, and the DC/DC or AC/DC converters.

❖ . Suited for power transformers, generators, motors, branch-points, or smaller busbar arrangements.

♦J*. Simple device operation using the integrated operator panel or a connected Personal computer running DIGSI® 4.

Differential Protection for Transformers

- . Current restraint tripping characteristic.

- . Stabilized against in-rush currents using the second harmonic.

❖. Stabilized against transient and steady-state fault currents caused e.g. by over excitation of transformers, using a further harmonic: optionally the third or fifth harmonic.

❖	. Insensitive against DC offset currents and current transformer saturation.

❖	High stability also for different current transformer saturation.

♦>. High-speed instantaneous trip on high-current transformer faults.

- Independent of the conditioning of the starpoint(s) of the power transformer.

- High earth-fault sensitivity by detection of the starpoint current of an earthed transformer winding.

- Integrated matching of the transformer connection group.

- Integrated matching of the transformation ratio including different rated currents of the transformer windings.

Differential Protection for Generators and Motors

♦>	Current restraint tripping characteristic.

- High sensitivity.

- Short tripping time.

♦>	Insensitive against DC offset currents and current transformer saturation.

- High stability also for different current transformer saturation.

- Independent of the conditioning of the starpoint.

Differential Protection for Mini-Busbars and Short Lines

- Current restraint tripping characteristic.

- Short tripping time.

❖	Insensitive against DC offset currents and current transformer saturation.
♦>	High stability also for different current transformer saturation.

♦>	Monitoring of the current connections with operation currents

Bus-Bar Protection

*> Single-phase differential protection for up to seven feeders of a busbar.

Either one relay per phase or one relay connected via interposed summation current transformers.

- Current restraint tripping characteristic.

- Short tripping time.

- Insensitive against DC offset currents and current transformer saturation. High stability also for different current transformer saturation.

- Monitoring of the current connections with operation currents

Restricted Earth Fault Protection

- Earth fault protection for earthed transformer windings, generators, motors, shunts reactors, or starpoint formers.

- Short tripping time.

♦> . High sensitivity for earth faults within the protected zone.

❖	High stability against external earth faults using the magnitude and phase relationship of through-flowing earth current

High-Impedance Unit Protection

♦>. Highly sensitive fault current detection using a common (external) burden

resistor. ♦t». Short tripping time.

❖	. Insensitive against DC offset currents and current transformer saturation. *l*. high stability with optimum matching.

*l*. Suitable for earth fault detection on earthed generators, motors, shunt reactors, and transformers, including auto-transformers.

❖	. Suitable for any voltage measurement (via the resistor current) for application of

high-impedance unit protection.

Tank Leakage Protection

- For transformers or reactors the tank of which is installed isolated or high resistive against ground.

- Monitoring of the leakage current flowing between the tank and ground.

❖	. Can be connected via a "normal" current input of the device or the special highly

sensitive current input (3 mA smallest setting).

Time Overcurrent Protection for Phase Currents and Residual Current

♦>. Two definite time delayed overcurrent stages for each of the phase currents and the residual (threefold zero sequence) current, can be assigned to any of the sides of the protected object.

❖	Additionally, one inverse time delayed overcurrent stage for each of the phase currents and the residual current.

♦♦♦ Selection of various inverse time characteristics of different standards is possible, alternatively a user defined characteristic can be specified.

❖	. All stages can be combined as desired; different characteristics can be selected for

phase currents on the one hand and the residual current on the other.

- . External blocking facility for any desired stage (e.g. for reverse interlocking). . Instantaneous trip when switching on a dead fault with any desired stage.

- . Inrush restraint using the second harmonic of the measured currents.

♦>. Dynamic switchover of the time overcurrent parameters, e.g. during cold-load startup of the power plant.

Time Overcurrent Protection for Earth Current

- Two definite time delayed overcurrent stages for the earth current connected at current input 17 (e.g. current between starpoint and earth).

- Additionally, one inverse time delayed overcurrent stage for the earth current.

❖	. Selection of various inverse time characteristics of different standards is possible,

alternatively a user defined characteristic can be specified. ♦♦♦ The stages can be combined as desired.

♦J*. External blocking facility for any desired stage (e.g. for reverse interlocking). . Instantaneous trip when switching on a dead fault with any desired stage.

❖	. Inrush restraint using the second harmonic of the measured current.

❖. Dynamic switchover of the time overcurrent parameters, e.g. during cold-load startup of the power plant.

Single-Phase Time Overcurrent Protection

♦.♦ Two definite time delayed overcurrent stages can be combined as desired. *l* . For any desired single-phase overcurrent detection.

❖ . Can be assigned to the current input 17 or the highly sensitive current input 18. ❖. Suitable for detection of very small current (e.g. for high-impedance unit

protection or tank leakage protection, see above). ♦> . Suitable for detection of any desired AC voltage using an external series resistor

(e.g. for high-impedance unit protection, see above). ❖. External blocking facility for any desired stage.

Unbalanced Load Protection

❖	. Processing of the negative sequence current of any desired side of the protected

object.

♦♦♦. Two definite time delayed negative sequence current stages and one additional inverse time delayed negative sequence current stage.

❖	. Selection of various inverse time characteristics of different standards is possible,

alternatively a user defined characteristic can be specified. *l*. The stages can be combined as desired.

Thermal Overload Protection

♦J*. Thermal replica of current-initiated heat losses. ♦♦♦. True RMS current calculation.

❖	. Can be assigned to any desired side of the protected object. ♦♦•. Adjustable thermal warning stage.

❖. Adjustable current warning stage.

❖	. Alternatively evaluation of the hot-spot temperature according to IEC 60354 with

❖	calculation of the reserve power and ageing rate (by means of external temperature sensors via thermo box).

Circuit Breaker Failure Protection

❖	With monitoring of current flow through each breaker pole of the assigned side of the protected object.

❖. Supervision of the breaker position possible (if breaker auxiliary contacts available).

<♦. Initiation by each of the internal protection functions.

❖	. Initiation by external trip functions possible via binary input.

External Direct Trip

- Tripping of either circuit breaker by an external device via binary inputs.

- Inclusion of external commands into the internal processing of information and trip commands.

- With or without trip time delay.

Processing of External Information

❖. Combining of external signals (user defined information) into the internal

information processing. ❖ Pre-defined transformer annunciations for Buchholz protection and oil gassing. ❖. Connection to output relays, LEDs, and via the serial system interface to a central

computer station.

User Defined Logic Functions (CFC)

❖. Freely programmable linkage between internal and external signals for the

implementation of user defined logic functions. ♦♦♦. All usual logic functions.

❖. Time delays and measured value set point interrogation.

Commissioning Operation

- . Comprehensive support facilities for operation and commissioning.

- . Indication of all measured values, amplitudes and phase relation.

- . Indication of the calculated differential and restraint currents.

♦J*. Integrated help tools can be visualized by means of a standard browser: Phasor diagrams of all currents at all ends of the protected object are displayed as a graph.

♦> . Connection and direction checks as well as interface check.

Monitoring Functions

❖	. Monitoring of the internal measuring circuits, the auxiliary voltage supply, as well

as the hard- and software, resulting in increased reliability. *l* Supervision of the current transformer secondary circuits by means of symmetry checks.

❖	. Check of the consistency of protection settings as to the protected object and the

assignment of the current inputs: blocking of the differential protection system in case of inconsistent settings which could lead to a malfunction. Trip circuit supervision is possible.

Further Functions

❖. Battery buffered real time clock, which may be synchronized via a

synchronization signal (e.g. DCF77, IRIG B via satellite receiver), binary

input or system interface. ❖ . Continuous calculation and display of measured quantities on the front of

the device. Indication of measured quantities of all sides of the protected

object.

❖. Fault event memory (trip log) for the last 8 network faults (faults in the power system), with real time stamps (ms-resolution).

- Fault recording memory and data transfer for analog and user configurable binary signal traces with a maximum time range of 5 s.

- Switching statistics: counter with the trip commands issued by the device, as well as record of the fault current and accumulation of the interrupted fault currents;

- Communication with central control and data storage equipment via serial interfaces through the choice of data cable, modem, or optical fibers, as an option.

PROTECION SCHEME USING NUMERICAL RELAY

DIFFERENTIAL PROTECTION FOR TRANSFORMERS

Matching of the Measured Values

In power transformers, generally, the secondary currents of the current transformers are not equal when a current flows through the power transformer, but depend on the transformation ratio and the connection group of the protected power transformer, and the rated currents of the current transformers at both sides of the power transformer. The currents must, therefore, be matched in order to become comparable. Matching to the various power transformer and current transformer ratios and of the phase displacement according to the vector group of the protected transformer is performed purely mathematically. As a rule, external matching transformers are not required. The input currents are converted in relation to the power transformer rated current. This is achieved by entering the rated transformer data, such as rated power, rated voltage and rated primary current of the current transformers, into the protection device. Once the vector group has been entered, the protection is capable of performing the current comparison according to fixed formulae. Conversion of the currents is performed by programmed coefficient matrices which simulate the difference currents in the transformer windings. All conceivable vector groups (including phase exchange) are possible. In this aspect, the conditioning of the starpoint(s) of the power transformer is essential, too.

Isolated Starpoint

Figure 2-15 illustrates an example for a power transformer Yd5 (wye-delta with 150 ° phase displacement) without any earthed starpoint. The figure shows the windings and the phasor diagrams of symmetrical currents and, at the bottom, the matrix equations. The general form of these equations is

Im = k.(K).In,

Where

(Im) - Matrix of the matched currents IA, IB. IC, k -    Constant factor,

(K) - Coefficient matrix, dependent on the vector group, (In) - Matrix of the phase currents IL1, IL2, IL3.

Winding 2Winding 1

Figure 2-15   Matching the transformer vector group, example Yd5 (magnitudes not considered)

On the left (delta) winding, the matched currents IA, IB, IC are derived from the difference of the phase currents I.L1, IL2, IL3. On the right (wye) side, the matched currents are equal to the phase currents (magnitude matching not considered).

Earthed Starpoint

Figure 2-16 illustrates an example for a transformer YNd5 with an earthed starpoint on the Y-side. In this case, the zero sequence currents are eliminated. On the left side, the zero sequence currents cancel each other because of the calculation of the current differences. This complies with the fact that zero sequence current is not possible outside of the delta winding. On the right side, the zero sequence current is eliminated by the calculation rule of the matrix, e.g.

l/3-(2 IL1 - 1 IL2- 1 IL3)= 1/3 • (3 IL1 - IL1 - 1L2 - IL3) = 1/3 • (3 IL1 -3 I0) = (1L1 -10).

Zero sequence current elimination achieves that fault currents which flow via the transformer during earth faults in the network in case of an earth point in the protected zone (transformer starpoint or starpoint former by neutral earth reactor) are rendered harmless without any special external measures. Refer e.g. to Figure 2-17: Because of the earthed starpoint, a zero sequence current occurs on the right side during a network fault but not on the left side. Comparison of the phase currents, without zero sequence current elimination, would cause a wrong result (current difference in spite of an external fault).

Figure 2-18 shows an example of an earth fault on the delta side outside the protected zone if an earthed starpoint former (zigzag winding) is installed within the protected zone. In this arrangement, a zero sequence current occurs on the right side but not on the left, as above. If the starpoint former were outside the protected zone (i.e. CTs between power transformer and starpoint former) the zero sequence current would not pass through the measuring point (CTs) and would not have any harmful effect.

The disadvantage of elimination of the zero sequence current is that the protection becomes less sensitive (factor 2/3 because the zero sequence current amounts to 1/3) in case of an earth fault in the protected area. Therefore, elimination is suppressed in case the starpoint is not earthed (see above, Figure 2-15).

Winding 2Winding 1

Figure 2-16  Matching the transformer vector group, example YNd5 (magnitudes not considered)

Li

Li

hm.

t52

rYY\

Figure 2-17  Example of an eann fault outside the protected transformer and current distribution

L-,

| \ |  | H |  |
| --- | --- | --- | --- |
| \ |  |  |  |
|  |  | J |  |

Figure 2-18   Example of an earth fault outside :ne protected transformer with a neutral earthing reactor within tie protected zone

Increasing the Ground Fault Sensitivity

Higher earth fault sensitivity in case of an earthed winding can be achieved if the starpoint current is available, i.e. if a current transformer is installed in the starpoint connection to earth and this current is fed to the device (current input 17). Figure 2-19 shows an example of a power transformer the starpoint of which is earthed on the Y-side. In this case, the zero sequence current is not eliminated. Instead of this, 1/3 of the starpoint current ISP is added for each phase.

1-1 •

3.

-e-

Li

u

=C7	J "-'3

7*"     H i

Figure 2-19  Example of a earth fault outside the transformer«

The matrix equation is in this case:

1=

= 1

1 0 0 0 1 0 0 0 1

|  | / \ |  |
| --- | --- | --- |
|  | 1 | Isp ■sp |
| IL2 | 3' |  |
| k-2 , |  |  |

ISP corresponds to -310 but is measured in the starpoint connection of the winding and not in the phase lines. The effect is that the zero sequence current is considered in case of an internal fault (from 10 = -1/3ISP), whilst the zero sequence current is eliminated in case of an external fault because the zero sequence current on the terminal side 10 = 1/3 • (IL1 + IL2 + IL3) compensates for the staipoint current. In this tway, full sensitivity (with zero sequence current) is achieved for internal earth faults and full elimination of the zero sequence current in case of external earth faults.

Even higher earth fault sensitivity during internal earth fault is possible by means of the restricted earth fault protection.

Use on Single- Phase Transformers

Single-phase transformers can be designed with one or two windings per side; in the latter case, the winding phases can be wound on one or two iron cores. In order to ■ensure that optimum matching of the currents would be possible, always two measured [: current inputs shall be used even if only one current transformer is installed on one phase. [The currents are to be connected to the inputs LI and L3 of the device; they are : designated IL1 and IL3 in the following.

If two winding phases are available, they may be connected either in series (which corresponds to a wye-winding) or in parallel (which corresponds to a delta-winding). The phase displacement between the windings can only be 0° or 180°. Figure 2-21 shows an example of a single-phase power transformer with two phases per side with Ithe definition of the direction of the currents.

-i       i.

■a

U      Li

L3

Figure 2-21   txantpie of a single-phase transformer with current definition

Like with three-phase power transformers, the currents are matched by programmed coefficient matrices which simulate the difference currents in the transformer windings.

The common form of these equations is Im = k.(K).In

Where

(Im) - matrix of the matched currents IA, IC,

k -   Constant factor,

(K) - coefficient matrix,

(In) - Matrix of the phase currents IL1, IL3.

Since the phase displacement between the windings can only be 0° or 180°, matching is relevant only with respect to the treatment of the zero sequence current (besides magnitude matching). If the "starpoinf of the protected transformer winding is not earthed (Figure 2-21 left side), the phase currents can directly be used.

If a "starpoinf is earthed (Figure 2-21 right side), the zero sequence current must be eliminated by forming the current differences. Thus, fault currents which flow through the transformer during earth faults in the network in case of an earth point in the protected zone (transformer "starpoint") are rendered harmless without any special external measures.

Ia= 11  0: Ili "I,..0 1

The matrices are (Figure 2-21):

| Ia | = 1 | 1 -i |  |  |
| --- | --- | --- | --- | --- |
| -c | *3 | -i 1 4 |  |  |

The disadvantage of elimination of the zero sequence current is that the protection becomes less sensitive (factor 1/2 because the zero sequence current amounts to 1/2) in case of an earth fault in the protected area. Higher earth fault sensitivity can be achieved if the "starpoint" current is available, i.e. if a CT is installed in the "starpoint" connection to earth and this current is fed to the device (current input 17).

U.

^Yl pry

U

IP

i

Figure 2-22   Example of an earth fault outside a single-phase transformer with current distribution

The matrices are in this case:

| f ^ |  |  | ■\ |  | ( \ | r |  |  | f \ |  | i % |  | f , |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ia | = 1 | 1 0 |  |  |  |  | h | = 1- | 1 0 |  |  | 1 | I I -sp |
|  |  | 0 1 (, | 1 |  | , II3 > |  |  |  | 0 1 |  | , -L3 ,, | *2' | 'sp J |

where ISP is the current measured in the "starpoint" connection.

The zero sequence current is not eliminated. Instead of this, for each phase 1/2 of the starpoint current ISP is added. The effect is that the zero sequence current is considered in case of an internal fault (from 10 = -1/2ISP), whilst the zero sequence current is eliminated in case of an external fault because the zero sequence current on the

cNcDfeei..cf«?

terminal side 10 = 1/2 • (IL1 + IL3) compensates for the "starpoint" current. In this way, full sensitivity (with zero sequence current) is achieved for internal earth faults and full elimination of the zero sequence current in case of external earth faults.

RESTRICTED EARTH FAULT PROTECTION

Figure 2-37   Restricted earth fault protection on a non-earthed transformer winding with neutral reactor (starsoint former) within the protected zone

The restricted earth fault protection detects earth faults in power transformers, shunt reactors, neutral grounding transformers/reactors, or rotating machines, the staipoint of which is led to earth. It is also suitable when a starpoint former is installed within a protected zone of a non-earthed power transformer. A precondition is that a current transformer is installed in the starpoint connection, i.e. between the staipoint and earth. The staipoint CT and the three phase CTs define the limits of the protected zone exactly.

rtgure 2-36  Restricted earth fault protection on an earthed transformer winding

Function Description Basic Principle

During healthy operation, no starpoint current ISP flows through the staipoint lead, the sum of the phase currents 310 = IL1 + IL2 + IL3 is zero, too. When an earth fault occurs in the protected zone (Figure 2-41), a starpoint current ISP will flow; depending on the earthing conditions of the power system a further earth current may be recognized in the residual current path of the phase current transformers.

Since all currents which flow into the protected zone are defined positive, the residual current from the system will be more or less in phase with the staipoint current.

rm

^1

■ U

if.3

Figure 2-41   E>:a"iole for an ears fault in a transformer with current disfibini

When an earth fault occurs outside the protected zone (Figure 2-42), a starpoint current ISP will flow equally; but the residual current of the phase current transformers 310 is now of equal magnitude and in phase opposition with the starpoint current.

Figure 2-42  Example for an earth fault outside a transformer with current distribution

When a fault without earth connection occurs outside the protected zone, a residual current may occur in the residual current path of the phase current transformers which is caused by different saturation of the phase current transformers under strong through-current conditions. This current could simulate a fault in the protected zone. Wrong tripping must be avoided under such condition. For this, the restricted earth fault protection provides stabilization methods which differ strongly from the usual stabilization methods of differential protection schemes since it uses, besides the magnitude of the measured currents, the phase relationship, too.

L

Evaluation of the Measured Quantities

The restricted earth fault protection compares the fundamental wave of the current flowing in the starpoint connection, which is designated as 310' in the following, with the fundamental wave of the sum of the phase currents, which should be designated in the following as 310". Thus, the following applies (Figure 2-43):

310' = ISP

310" - ILI +IL2 + IL3 Only 310' acts as the tripping effect quantity, during a fault within the protected zone this current is always present.

rY

LI + lL-2

"1

Li

tL

7UT61

Figure 2-43  Prno'cle of restricted earth fault protection

When an earth fault occurs outside the protected zone, another earth current 310" flows though the phase current transformers. This is, on the primary side, in counterphase with the starpoint 310' current and has equal magnitude. The maximum information of the currents is evaluated for stabilization: the magnitude of the currents and their phase position. The following is defined: A tripping effect current

IREF = |3I0'| and the stabilization or restraining current

IRest = k • (|3I0' - 3I0"| - |3I0' + 3I0"|)

where k is a stabilization factor which will be explained below, at first we assume k = 1. IREF is derived from the fundamental wave and produces the tripping effect quantity, IRest counteracts this effect.

To clarify the situation, three important operating conditions should be examined: a) Through-fault current on an external earth fault:

310" is in phase opposition with 310' and of equal magnitude i.e. 310" = -310' IREF = |3I0'|

IRest = |3I0* + 3I0"| - |3I0' - 3I0"| = 2(310*1

The tripping effect current (IREF) equals the starpoint current; restraint (IRest) corresponds to twice the tripping effect current.

b)	Internal earth fault, fed only from the starpoint:

In this case, 310" = 0	I

IREF - |3I0'|

IRest = |310' -0H3I0' + 0| = 0

The tripping effect current (IREF) equals the starpoint current; restraint (IRest) is zero, i.e. full sensitivity during internal earth fault.

c)	Internal earth fault, fed from the starpoint and from the system, e.g. with equal
earth current magnitude:

In this case, 310" = 310' IREF = |3I0'|

IRest = |3I0' - 3I0*| - |3I0' + 3I0'| = -2 • |3I0'|

I

The tripping effect current (IREF) equals the starpoint current; the restraining quantity (IRest) is negative and, therefore, set to zero, i.e. full sensitivity during internal earth fault.This result shows that for internal fault no stabilization is effective since the restraint quantity is either zero or negative. Thus, small earth current can cause tripping. In contrast, strong restraint becomes effective for external earth faults. Figure 2-44 shows that the restraint is the strongest when the residual current from the phase currenttransformers is high (area with negative 3I073I0'). With ideal current transformers, 3107310' would be -1.

If the starpoint current transformer is designed weaker than the phase current transformers (e.g. by selection of a smaller accuracy limit factor or by higher secondary burden), no trip will be possible under through-fault condition even in case of severe saturation as the magnitude of 310" is always higher than that of 310'.

Flipping

3Blockii"J        \

-0.3-93-0 1cdo.t0.2 —». 3i°' 0.3

3Io'

Figure 2-44  Tripping characteristic of the restricted earth fault protection depending on the earth current ratio 3Iq73Id' (both currents in phase + or counter-phase -); IRE= = tripping effect current;       = setting value

The restraint quantity can be influenced by means of a factor k. This factor has certain relationship to the limit angle jlimit. This limit angle determines, for which phase displacement between 310" and 310' the pickup value grows to infinity when 310" = 310', i.e. no pickup occurs. In 7UT612 is k = 2, i.e. the restraint quantity in the above example a) is redoubled once more: the restraint quantity IRest is 4 times the tripping effect quantity IREF. The limit angle is jlimit = 110°. That means no trip is possible for phase displacement j(3I0"; 310') 3 110°. Figure 2-46 shows the operating characteristics of the restricted earth fault protection dependent of the phase displacement between 310" and 310', for a constant in feed ratio |3I0"| = |3I0'|.

'F.EF IF= = >

AT■ippingBlockii,.

120-110'1D0«W"*     ^Sl^lLl

Figure 2-46   Tripping characteristic of the restricted earth fault protection depending on the phase displacement between     and %' at 3%" = 3y (180* = external fault)

PICK-UP/TRIPPING

:.3i i \ i-mf'

i3| SLOPE

I^?5817	, r

(REF picked upj-—

— - 	 ■ -|

pui+iluUtluMW

L .

I 13121T 1-603 g

0

I	1

W	I

FNo 05821 -$EFTRIP

| i3CtflEF P ROT. |

I    8iecft rsia/

=No 05603 J>3LOCK REF"'

6s

FNo 05812 SLCChEpi

FNo 55613 -fREF ACTIVE >

FNo 05811 -C REF OFF   )

Figure 2-48  Logic diagram of the restricted earth fault protection

As soon as the fundamental wave of the differential current reaches 85% the set value or the stabilizing current exceeds 4 times the rated transformer current the protection picks up. If the trip condition are fulfilled trip signal is issued. Reset of pick up is initiated when the differential current has fallen below 70% of set value. If a trip command has not been initiated, the fault is considered to be over. If trip command has been formed, then a timer or a settable duration can be started upon reset of pick up. During this time the trip command is held in.

TIME OVERCURRENT PROTECTION FOR PHASE AND RESIDUAL CURRENTS

General

The time overcurrent protection is used as backup protection for the short-circuit protection of the protected object and provides backup protection for external faults which are not promptly disconnected and thus may endanger the protected object.

The time overcurrent protection for phase currents takes its currents from the side to which it is assigned. The time overcurrent protection for residual current always uses the sum of the current of that side to which it is assigned. The side for the phase currents may be different from that of the residual current.

The time overcurrent protection provides two definite time stages and one inverse time stage for each the phase currents and the residual current. The inverse time stages may operate according an IEC or an ANSI, or an user defined characteristic.

Function Description

Definite Time Overcurrent Protection

The definite time stages for phase currents and residual current are always available even if an inverse time characteristic has been configured.

Pickup, Trip

Two definite time stages are available for each the phase currents and the residual current (3 TO). Each phase current and the residual current 3 -10 are compared with the setting value ,I» (common setting for the three phase currents) and 3I0» (independent setting for 3T0). Currents above the associated pickup value are detected and annunciated. When the respective delay time T I» or T 3I0»is expired, tripping command is issued. The reset value is approximately 5 % below the pickup value for currents > 0.3 • IN.

Each phase current and the residual current 3-10 are, additionally, compared with the setting value ,I.> (common setting for the three phase currents) and 3I0> (independent setting for 3-10). When the set thresholds are exceeded, pickup is annunciated. But if inrush restraint is used a frequency analysis is performed first. If an inrush condition is detected, pickup annunciation is suppressed and an inrush message is output instead. When, after pickup without inrush recognition, the relevant delay times 7_,! or

7	,_! are expired, tripping command is issued. During inrush condition no trip is

possible but expiry of the timer is annunciated. The reset value is approximately 5 % below the pickup value for currents > 0,3-IN.

I inactive

l'

I'

1 is mstsMt,

FNo7551 FMq 7?6f.... 7587

-toC Phase OFF"

Figure 2-50   Logic diagram of the overcurrent stages I> for phase currents

Figure A shows the logic diagram of the stages I> for phase currents

Figure B shows the logic diagram of over current stage 3I0> for residual current.

l:'30g|3I0 >'AN, CL05E~|

I Inactive

I 3/0>> instant.

I aJOp instant. N3/0> imtsnt.

IM.t. Pes?■■

rr _■

-\HB> InRush PU.;

jEfiteiaa	v

RJot7» ..

It 3to-l

-IQ/C 310 PU	J

FMO1&04 H^3|[)> picked ug)

FNo1&06

FNolWS —C3I0> Tkb« Out~:

FNo1741

~x ■	
V Mess. release

/No 1S57 FN0 1749

12201 bio Q,c  I

I

S

1-

"t&'C3!P 8LK_ FNoi7»

f No VAi

-Coc :^7p-F ';

Figure 2-51   Logic diagram of me overcyrrenf stage 3%» for residua! current

The pickup values for each of the stages, I> (phase currents), 3I0> (residual cuirent), I» (phase currents), 3I0» (residual current) and the delay times can be set individually.

Inverse Time Overcurrent Protection

The inverse time overcurrent stages operate with a characteristic either according to the IEC- or the ANSI-standard or with a user-defined characteristic. When configuring one of the inverse time characteristics, definite time stages I» and I> are also enabled.

Pickup, Trip

Each phase current and the residual current (sum of phase currents) are compared, one by one, to a common setting value Ip and a separate setting 3I0p. If a current exceeds 1.1 times the setting value, the corresponding stage picks up and is signaled selectively. But if inrush restraint is used a frequency analysis is performed first. If an inrush condition is detected, pickup annunciation is suppressed and an inrush message is output instead. The RMS values of the basic oscillations are used for pickup. During the pickup of an Ip stage, the tripping time is calculated from the flowing fault current by means of an integrating measuring procedure, depending on the selected tripping characteristic. After the expiration of this period, a trip command is transmitted as long as no inrush current is detected or inrush restraint is disabled. If inrush restraint is enabled and inrush current is detected, there will be no tripping. Nevertheless, an annunciation is generated indicating that the time has expired. For the residual current 3I0p the characteristic can be selected independent from the characteristic used for the phase currents. The pickup values for the stages Ip (phase currents), 3I0p (residual current) and the delay times for each of these stages can be set individually.

Figure 2-52 shows the logic diagram of the inverse time stages for phase currents.

f,r.*;aj MANUAL  -t Off active

FNo 1751

:re 2-52    Logic diagram c>* the inverse time overcurrent stages Ip for p^isse currents — example for tEC—curves

K.J.* InRuth g<J . X

Figure 2-53 for residual current.

■ ■    -:i HI

JI'.' ■ ■ intxant. , 310n instant.

', 3W> instant.

1 n>

FHz 1744

-| ItC curve

|..': :'|t aiop |

\L M-,-,i-, release

,FEJ3 757Q -:>Qp )rRj%H PU) FNo75e|_

FNo 8766 -(0/5 380 PU    j| FNo t«ST

—(,.3IOp pickedjg>J

FNc !60a -CllOp TR|P~~~3

FNo 1908 -C3J6p'flm«but'";

FNc 1859

FNo 1741

J>3LK 310Q."C

13x0 C c I

.1^

>l

- t 1 sl:.c- cq

FN© 1748

'J ; il3 SLK~)

FNo i7M__

-yO/C 310 ACffVfe FNo J74S

-(oq|wr)

Figure 2-53   Lojic diagram of the inverse time overcurrent stage for residual current — exams le ?or lEC-curves

THERMAL OVERLOAD PROTECTION

The thermal overload protection prevents damage to the protected object caused by thermal overloading, particularly in case of power transformers, rotating machines, power reactors and cables.

OVERLOAD PROTECTION USING A THERMAL REPLICA Principle

The thermal overload protection of 7UT612 can be assigned to one of the sides of the protected object (selectable), i.e. it evaluates the currents flowing at this side. Since the cause of overload is normally outside the protected object, the overload current is a through-flowing current. The unit computes the temperature rise according to a thermal single-body model as per the following thermal differential equation

de/dt + (1/Tth)e = 1/ rth(I/k.lNobj)2

with    currently valid temperature rise referred to the final temperature rise for the

maximum permissible phase current k • INobj, xth - thermal time constant for heating up,

k - k-factor which states the maximum permissible continuous current, referred to

the rated current of the protected object, I - currently valid RMS current, INobj - rated current of protected object.

The solution of this equation under steady-state conditions is an e-function whose asymptote shows the final temperature rise 9end- When the temperature rise reaches the first settable temperature threshold 9aiarm, which is below the final temperature rise, a warning alarm is given in order to allow an early load reduction. When the second

temperature threshold, i.e. the final temperature rise or tripping temperature, is reached, the protected object is disconnected from the network. The overload protection can, however, also be set on Alarm Only .In this case only an alarm is output when the final temperature rise is reached.

The temperature rises are calculated separately for each phase in a thermal replica from the square of the associated phase current. This guarantees a true RMS value measurement and also includes the effect of harmonic content. The maximum calculated temperature rise of the three phases is decisive for evaluation of the thresholds. The maximum permissible continuous thermal overload current Imax is described as a multiple of the rated current INobj:

Imax = k • INobj	where INobj is the rated current of the protected object:

*l* For power transformers, the rated power of the assigned winding is decisive. The device calculates this rated current from the rated apparent power of the transformer and the rated voltage of the assigned winding. For transformers with tap changer, the non-regulated side must be used.

*t* For generators, motors, or reactors, the rated object current is calculated by the device from the set rated apparent power and the rated voltage.

❖ For short lines or busbars, the rated current was directly set.

In addition to the k-factor, the thermal time constant tth as well as the alarm temperature rise Qalarm must be entered into the protection.

Apart from the thermal alarm stage, the overload protection also includes a current overload alarm stage Iaia™, which can output an early warning that an overload current is imminent, even when the temperature rise has not yet reached the alarm or trip temperature rise values. The overload protection can be blocked via a binary input. In doing so, the thermal replica is also reset to zero.

Function Description General

The circuit breaker failure protection provides rapid backup fault clearance, in the event that the circuit breaker fails to respond to a trip command from a feeder protection. Whenever e.g. the differential protection or any short-circuit protection relay of a feeder issues a trip command to the circuit breaker, this is repeated to the breaker failure protection (Figure 2-81). A timer T-BF in the breaker failure protection is started. The timer runs as long as a trip command is present and current continues to flow through the breaker poles.

Fig:- Simplified function diagram of circuit breaker failure protection with current flow monitoring

Normally, the breaker will open and interrupt the fault current. The current monitoring stage CB-I> resets and stops the timer T-BF. If the trip command is not carried out (breaker failure case), current continues to flow and the timer runs to its set limit. The breaker failure protection then issues a command to trip the backup breakers and interrupt the fault current.

PROCESSING OF EXTERNAL SIGNALS

FUNCTION DESCRIPTION

External Trip Commands

Two desired trip signals from external protection or supervision units can be incorporated into the processing of the differential protection 7UT612. The signals are coupled into the device via binary inputs. Like the internal protection and supervision signals, the can be annunciated, delayed, transmitted to the output trip relays, and blocked. This allows to include mechanical protective devices (e.g. pressure switch, Buchholz protection) in the processing of 7UT612.

The minimum trip command duration set for all protective functions are also valid for these external trip commands. Figure shows the logic diagram of one of these external trip commands. Two of these functions are available. The function numbers FNo are illustrated for the external trip command 1.

FNo 04536

(Ext' pkker vz   )

rHo04f>2«

8602 T BELAY

FNo 04537

<ExH Guar TUP*)

_ FNo 04523

1 •»BLOCK ExtT>

FNo 04532

Transformer Messages

In addition to the external trip commands as described above, some typical, messages from power transformers can be incorporated into the processing of the 7UT612 via binary inputs. This prevents the user from creating user specified annunciations. These messages are the Buchholz alarm, Buchholz trip and Buchholz tank alarm as well as gassing alarm of the oil.

Blocking Signal for External Faults

Sometimes for transformers so-called sudden pressure relays (SPR) are installed in the tank which are meant to switch off the transformer in case of a sudden pressure increase. Not only transformer failures but also high traversing fault currents originating from external faults can lead to a pressure increase.

External faults are quickly recognized by 7UT612. A blocking signal can be created by means of a CFC logic in order to prevent from erroneous trip of the SPR.

MONITORING FUNCTIONS

The device incorporates comprehensive monitoring functions which cover both hardware and software; the measured values are continuously checked for plausibility, so that the CT circuits are also included in the monitoring system to a large extent. Furthermore, binary inputs are available for supervision of the trip circuit.

FUNCTION DESCRIPTION

Hardware Monitoring

The complete hardware including the measurement inputs and the output relays is monitored for faults and inadmissible states by monitoring circuits and by the processor.

Auxiliary and Reference Voltages

The processor voltage is monitored by the hardware as the processor cannot operate if the voltage drops below the minimum value. In that case, the device is not operational. When the correct voltage has re-established the processor system is restarted. Failure or switch-off of the supply voltage sets the system out of operation; this status is signaled by a fail-safe contact. Transient dips in supply voltage will not disturb the function of the relay. The processor monitors the offset and the reference voltage of the ADC (Analog-to Digital Converter). In case of inadmissible deviations the protection is blocked; persistent faults are signaled.

Memory Modules

All working memories (RAMs) are checked during start-up. If a fault occurs, the start is aborted and an LED starts flashing. During operation the memories are checked with the help of their checksum. For the program memory (EPROM), the cross-check sum is cyclically generated and compared to a stored reference program cross-check sum. For the parameter memory (EEPROM), the cross-check sum is cyclically generated and compared to the cross-check sum that is refreshed after each parameterization change. If a fault occurs the processor system is restarted.

SOFTWARE MONITORING Watchdog

For continuous monitoring of the program sequences, a watchdog timer is provided in the hardware (hardware watchdog) which will reset and completely restart the processor system in the event of processor failure or if a program falls out of step. A further software watchdog ensures that any error in the processing of the programs will be recognized. Such errors also lead to a reset of the processor.

If such an error is not eliminated by restarting, another restart attempt is initiated. If the fault is still present after three restart attempts within 30 s, the protection system will take itself out of service, and the red LED "Blocked" lights up. The "Device OK" relay drops off and signals the malfunction by its healthy status contact.

FAULT RECORDING

The differential protection 7UT612 is equipped with a fault recording function. The instantaneous values of the measured quantities

insi, iL2si, iL3si, ins2, 1l2S2, Jl3S2, 3iosi, 3ios2,17, k, and

iDiffLi, lDiffL2, lDifTL3, Wli, lRestL2, lRestL3 are sampled at 12/3 ms intervals (for a frequency of 50 Hz) and stored in a cyclic buffer (12 samples per period). When used as single-phase busbar protection, the first six feeder currents are stored instead of the phase currents, the zero sequence currents are nor applicable.

During a system fault these data are stored over a time span that can be set (5 s at the longest for each fault record). Up to 8 faults can be stored. The total capacity of the fault record memory is approx. 5 s. The fault recording buffer is updated when a new fault occurs, so that acknowledging is not necessary. Fault recording can be initiated, additionally to the protection pickup, via the integrated operator panel, the serial operator interface and the serial service interface.

The data can be retrieved via the serial interfaces by means of a personal computer and evaluated with the protection data processing program DIGSI® 4 and the graphic analysis software SIGRA 4. The latter graphically represents the data recorded during the system fault and calculates additional information from the measured values. A selection may be made as to whether the measured quantities are represented as primary or secondary values. Binary signal traces (marks) of particular events e.g. "fault detection", "tripping" are also represented.

If the device has a serial system interface, the fault recording data can be passed on to a central device via this interface. The evaluation of the data is done by the respective programs in the central device. The measured quantities are referred to their maximum values, scaled to their rated values and prepared for graphic representation. In addition, internal events are recorded as binary traces (marks), e.g. "fault detection",

"tripping". Where transfer to a central device is possible, the request for data transfer can be executed automatically. It can be selected to take place after each fault detection by the protection, or only after a trip.

m

£5 Fie Edit Insert View Options Window Help

f- <$-iiiiu FT ;Q.|ioo* jJliJB I; Avfr        proiie>

|  | trims | Measuring Signal | Instantaneous | R.M.S. | Name: TR111 Folder 7SJ612V4 4 Var.OC, j Filename: C:\SIEMENS\piGSI4\D4PR0J\tR- |
| --- | --- | --- | --- | --- | --- |
| Cursor!: | 507 | 11 | -226 A | 157 A |  |
| ,: Cursor 2 | 507 | iEs | ■0.86 A | 1.06 A |  |
| Delta(C2-C1): | 0.0 | iEs - a_i | 225 A | ■155 A |  |

d

ies/kft -.

|  | i |  |
| --- | --- | --- |
|  |  | 0.1 0.2 0.3 0.4 0.5 0.6 0 7 \ 0.8 ^S 1 ! r- 1 r— \ 1 — |
| •0.2 -0.1 i -C i—i——i | 0 |  |

| For Help, press Fl. |  |  | Primary fn,50.0Hz ;S.:---^/iut)AS;-v]i.u"Aifta8Wz |  |  |
| --- | --- | --- | --- | --- | --- |
| t start |  | ^ DIGSI Manager-TR111 ¦ | '} DIGSI - TR111 / Folder /.., | ^ sigra 4 - [time sign- |  |

fri File Edit Insert View Options Window Help

MM JIM

6-ill fciSlfcf; 'Q, |100% Jllfjlj ji I \ ;|r I ^Ncurrentprofile)

| Name: TR111 Filename: C:\SIEMENS\DIGSI4\D4PR0J\TR- | linms | Measuring Signal ¦ Instantaneous |  | RMS. |
| --- | --- | --- | --- | --- |
| Cursor 1: | 50.7 | LI | -226 A | 157 A |
| Cursor 2 | 507 | iEs | -0.86 A | 1.06 A |
| Delta(C2-Cn | 0.0 | is;-LI | 225 A | -155 A |

?SJ612V4.4Var,0(

n

>Tiig.Wave.Cap. Flag Lost O/C Ph L1 PU 0/C.Ph L2 PU O/C Pll L3 PU 0/C Earth PU Overcurrent PU OvetcurrentTRIP l>> TRIP l>TRIP Ip TRIP IE»TRIP IE> TRIP lEp TRIP lEE^TRIP IEE>TRIP lEEpTRIP Relay PICKUP Relay TRIP

■0.2

-0.0        o.i

0i	0.3

0.4

0.5

0.7

0.8

tfe

Primary :fn: 50.0 Hz ;pri.: —      a |Sec.: — V/1.0 a if: 0.8 W-fe

For Help, press Fl.

|« %!fj[ 4:14 PM

jj start) JJ <§ J » j5[DIGSU>tanag...] j DIG5i-TRll.,||sigra4-[...  8] Details of dis. ■ ■ j @] Document 1 -...

CONCLUSION

Transformer protection using numerical relays is the modem version of protection. Numerical relays has got several advantages as compared to ordinary electromagnetic relays. Through our project, we were able to analyze the existing" transformer protection system in BPCL Kochi Refinery. Even though the chances of faults occurring on them are very rare, the consequences of even a rare fault may be very serious unless the transformer is quickly disconnected from the system. This necessitated providing adequate automatic protection for transformer against possible faults.

www.siemens.com

www.en.wikipedia.org

www.IEEexplore.IEEE.org

REFERENCES