## Slide 1: Project presentation on OPTIMUM DESIGN OF AN ACOUSTIC ENCLOSURE FOR DIESEL GENERATOR
Notes: <number>

## Slide 2: What is an acoustic enclosure ?
An acoustic enclosure is a containerized vessel used for housing generators to :
Reduce noise levels.
Improve reliability and durability of generator sets (gensets).
Easy serviceability.
High uptime of genset.
Improved aesthetic of genset.
Better working conditions.
Notes: <number>

## Slide 3: Acoustic enclosures
Notes: <number>

## Slide 4: Problem statement
Optimum design of an acoustic enclosure for a diesel generator set (Ratings: 125 kVA) which satisfies the following clauses:
The enclosure should act as a containerised portable vessel along with the generator set (DG set) feasible to be used for frequent mobile applications.
Proper air ventilation for DG set should be available.
Noise reduction achieved should be achieved as specified under the CPCB Norms.
Notes: <number>

## Slide 5: Design data specifications:
Genset model : Cummins DB 125
(diesel)
Genset rating : 125kVA
Current (Amp) : 179
Fuel consumption: 149 gm/kW-hr
Length (mm) : 2225
Width (mm) : 925
Height (mm) : 1600
Weight (Kg) : 1370
Engine BHP : 154
No.of cylinders : 6
RPM : 1500
Cooling : Water cooled
Notes: <number>

## Slide 6: Presentation details
Introduction
Problem definition
Result comparison
Structure design
Air ventilation
Sound proofing
Future scope
References
Notes: <number>

## Slide 7: Results
Characteristics | Regular enclosure | Modified enclosure
Number of enclosure frame parts | 2 parts : 1 enclosure and 1 base frame | 1 single containerized enclosure
Weight |  | 25% reduction in weight
Lifting nodes | Variable | 482 mm from each of the base corners
Air ventilation | 6 mm of back pressure | 4.7 mm of back pressure
Sound proofing | Varies according to packing | Sound reduction upto 71 dB
Notes: <number>

## Slide 8: ENCLOSURE STRUCTURE DESIGN

## Slide 9: NEED FOR STRUCTURE DESIGN
Preventing escape of sound to surrounding
Earlier enclosure has to be installed on site around the fixed generator
Now a days enclosure are made such that they contain the generator inside
Thus can be moved as a single unit
To optimize proper lifting points
Selection of proper beams and columns

## Slide 10: DESIGN PROCEDURE
MATERIAL SELECTION FOR FRAME
SELECTION OF IDEAL C/S FOR CHANNELS
CREATING FEM MODEL OF ENCLOSURE FRAMEWORK
OPTIMIZATION PROCESS
ENCLOSURE LIFTING NODES
CHANNEL DIMENSION SELECTION

## Slide 11: Raw material selection
Material selection initially can be arbitrary.
For acoustic enclosures, as per design analysis, the material selected should be such that it has:
. Good strength and rigidity preventing failures lifting, transporting, and working conditions.
. Ease of manufacturability (fabrication, assembly)
. Structural reliability for a prolonged life with minimum maintenance
cost
. Structural compliance with IS standards (including safety regulations,
FOS, Pollution norms)
STEELS , preferably heat treated steel AISI1020 is used for rigid structures because of their good strength, ductility, availability,
weld ability and highest scrap value.
Notes: <number>

## Slide 12: Selection of frame columns & beams
Columns and beams are selected based upon their cross-sections.
By using identical dimensions for different cross-sectional columns or beams like I-section, L-section and []- section, the one with better strength can be selected
Material is same ,therefore bending stresses are assumed to be same
Using the formula:
Strength (M) = bending stress (P) * section modulus (Z)
Thus strength is directly proportional to section modulus and the section with greater value of Z is selected.
Hollow rectangular channel gives the better strength
Notes: <number>
Z=

## Slide 13
Material selected is AISI 1020
Selecting ideal C/S of channels :
Moment of resistance (strength)
M = σb * Z
= σb * (I/y)
Consider various shapes of channel to calculate m.o.i :
For hollow rectangular section,
I = (BD3/12) – (bd3/12)
= ((100*1803)/12) – ((92*1723)/12)
= 95.8 * 105 mm4

## Slide 14
For I section,
Ixx = ((B*D3)/12)-((b*d3)/12)
= ((100*1803)-(92*1803))/12
= 48600000-44712000
= 38.8*105 mm2
For C channel,
By area method,
Co-ordinates for centroid of section
X = 25248/2112
= 11.95
Y = 90
So, I = 59.68*105 mm4

## Slide 15: FINITE ELEMENT METHOD
ANSYS 10 is used
Model created in ANSYS (fig showing structure model using BEAM44 of hollow rectangular C/S)

## Slide 16: METHODOLOGY OF FEA
Discretize the continuum
Select interpolation function
Find the element properties
Assemble the element properties to obtain the system equations
Impose the boundary
conditions
Solve the system
equations

## Slide 17
Taking the genset load at predefined nodes and lifting supports at 4 end nodes of enclosure we can analyze the system for maximum and minimum stresses as follows:

## Slide 18: OPTIMIZATION PROCESS
The sub-problem approximation method is used
Max allowable stress is 84 MPa
Maximum feasible and infeasible sets for iteration are chosen 100 and 80 respectively
Quadratic curve fitting polynomial function is chosen for design and state variables for next iteration
Design variable: 5 ≤ t ≤ 12.2
0 ≤ LOCX1 ≤ 2000
State variable: 10 ≤ MAXSTRESS ≤ 84
Objective function: weight=dens *(2*B*t+2*(D- 2*t)*t*(4000*4+1600*6+2000*4))
Where, dens =density of AISI 1020 i.e. 7850 kg/m3

## Slide 19
Design Optimization
From above analysis we obtain maximum stress in the entire structure as 53.511 MPa and the feasible nodes are for lifting are at a distance 482 mm from all base nodes.
The optimum thickness value obtained is 6.2 mm.
The analysed result obtained can be formulated on graph as follows:

## Slide 20
Notes: <number>

## Slide 21: OPTIMIZATION RESULT referring to ISMC codes
For thickness (mm) | D(mm) x B(mm) (Type of section) | Weight/mtr (Kg/m)
6.4 | 152 x 76 (RSC) | 17.88
6.4 | 127 x 64 (RSC) | 14.9

## Slide 22
FEA of Final Optimization Result of channel selection 127 x 64 RSC (failed)
FEA of Final Optimization Result of channel selection 152 x 76 RSC (correct)

## Slide 23: The optimum channel selection is 152 x 76 RSC of material AISI 1020
Graph for optimized result
Notes: <number>

## Slide 24: AIR VENTILATION
Notes: <number>

## Slide 25
Notes: <number>

## Slide 26: Cross ventilation and fresh air is must for satisfactory operation of genset. Air should flow from alternator to engine end.
As air flows through enclosure, its temperature increases. This increase is difference between temperature measured at alternator and at outdoor. The maximum allowed temperature rise is limited to 5oC to 10oC.
Notes: <number>

## Slide 27: The Required air flow rate to keep specific temperature rise in control can be calculated as : ma =
where,
  ma = mass flow rate of air into enclosure
Q = heat rejection into enclosure (25kW)
Cp = specific heat (0.017 kW/˚C)
∆T = temperature rise in enclosure (5 ˚C)
ρ = density of air (1.099 kg/m3)
Notes: <number>

## Slide 28: So, for ∆T=5 o C, we require mass flow rate of air of about 4469.30 lit/sec. To allow this air flow in the enclosure, we need proper inlet and outlet openings without any compensation in soundproofing. Also, care has to be taken that, at high velocities of radiator fan, there should be no suction of rain water, dirt, debris or any other unwanted elements with the air .
To achieve such opening, which allows only air to pass with minimum foreign particles ‘LOUVERS’ are used.
Notes: <number>

## Slide 29: A louver is a ventilation product that allows air to pass through it while keeping out unwanted elements
The basic consideration for louver section are :-
Free Area
Water penetration
Resistance to air flow
Fig.- Louver
Notes: <number>

## Slide 30: Free area is derived by taking the total open area of a louver and dividing by the overall wall opening. Generally, it is taken as 35% to 60%.
First Point of Water Penetration is the point at which a louver allows the passage of water through the louver.
Fig.- Free Area for Air Flow
Fig.
Good Water Resistance Louver
Notes: <number>

## Slide 31
Every obstruction in the airstream creates resistance, which reduces velocity of air flow. The resistance of the louver can be measured by running air through the louver and measuring the pressure differential at various free area velocities. Lower blade angles or more aerodynamic shapes create less resistance.
Fig. - Resistance to Air Flow
Notes: <number>

## Slide 32
For proper enclosure ventilation our objective is to select louver dimensions for both inlet and exit keeping in mind :
The company standards
Prescribed static pressure
Louver considerations
Fig.- Path of Air Flow through Louver
Notes: <number>

## Slide 33: Selection of louver material
Apart from steel most commonly used louver material today is the aluminium AISI 6063 T5 because of the following reasons:
Light weight construction.
Feasible mounting for various opening types.
Architectural surface finishes provides minimum drag against air flow.
It can sustain higher wind loads of up to 100mph.
Able to withstand high temperatures of air about 600 to 650˚C.
Notes: <number>

## Slide 34: Calculation procedure
Find louver free area
Refer company standards and free area chart to get louver dimensions
Opening for inlet is done on either sides of enclosure as shown in the diagram
Find rear exit louver dimensions (2.5 to 3 times the radiator core)
Find front inlet louver dimensions (1.5times the radiator core )
Obtain final louver dimensions
Check for back pressure < 6mm of water column
Notes: <number>

## Slide 35: Final louver dimensions
Louver opening | Number | Dimensions
Inlet air louver | 2 ( 1 on either side ) | 0.3x1.8 sq.m
Exit air louver | 1 | 0.90x1.20 sq.m
Notes: <number>

## Slide 36: SOUND PROOFING

## Slide 37: TARGET
Reduce the maximum sound power level of 97dB to 71 dB at distance of 1 meter from all sides of enclosure.

## Slide 38: NOISE PREDICTION METHOD (theoretical)
This method can predict level of noise with acceptable engineering accuracy over the frequency range 50-5,000 Hz using simple and readily available expressions.
According to experiments performed by National Research Council (NRC) in Canada the difference between practical measurement and theoretical noise prediction is less than 0.5dB and 90% of results were found to lie within ± 2.5 dB.

## Slide 39: CONCEPT AND FORMULA USED
Formulae used:
L = Lρ – TL + 10Log(S/A) – 20Log(r) – 8.......................1)
TL = 20 Log (n*t*freq) - 47............................................... 2)
A = α · S ...........................................................................3)

## Slide 40
F
L
O
W
C
H
A
R
T

## Slide 41: ADVANTAGE & LIMITATION
This method uses the design data about a newly developed enclosure to simulate its noise.
Frequency range is taken into consideration.
Ease of use.
Accuracy of method is less as it does not taking into account the Insertion losses(IL) & only consider transmission losses(TL). Insertion loss models are still under research.

## Slide 42: CONSIDERED WITH STEEL &ALUMINIUM PLATE
a)Polyethylene foam
( Density = 36.84kg/m3)
b) Armaflex foam
(Density = 40.045 kg/m3)
c) Coir fibre foam
(Density = 74 kg/m3)
d) Rockwool
( Density = 36.84kg/m3)
e) Steel plate
(Density = 7850kg/m3)
f) Aluminium plate
(Density = 2700kg/m3)

## Slide 43: MATERIAL FOUND DESIRABLE BASED ON THE ITERATION

## Slide 44: Future scope
Study and development of optimization code by combining the following aspects for acoustic enclosure:
Optimum Weld thickness to be used
Computational fluid dynamics of flow of air through enclosure
Thermo-structural analysis to study effective heat transfer around the DG set in the enclosure
Development of insertion loss model for acoustical treatment at the sound source. At present transmission losses of 25 dB have been achieved from the various acoustical materials applied to the enclosure body. But, additional sound reduction of up to 10 dB can be achieved using insertion loss phenomenon.
Notes: <number>

## Slide 45: REFERENCES:
BOOKS
Mechanical Engineering Design, by Joseph E. Shingley, Pg. 933, 983.
Design of Machine Elements, by V. B. Bhandari, Pg. 1 to 82, 22 to 57, 71 to 85.
Structural Design and Drawing, by N. Krishna Raju, Pg. 199 to 203.
Structural Engineering for Architecture, by A. P. Dongre, Pg. 13.1 to 13.8.
Statics and Strength of Material (Foundation for Structural Design), by Barry Onouye, Pg. 151to 261, 415.
Mechanical Vibrations and Noise Engineering, by A. G. Ambekar, Pg. 343 to 384.
JOURNALS
Diesel Engines Technical Data, published on Aug 1998(Company Confidential).
Reciprocating internal Combustion Engines (British Standard Controlled).
Application Manual-Liquid Cooled Generator Sets (Company Confidential).
Engine Installation Recommendation (Company Confidential).
Genset Installation Recommendation (Company Confidential).
Notes: <number>

## Slide 46
PAPERS
Optimal Design of an Enclosure for a Portable Generator, by
Joseph E. Blanks.
Development of Technique to Predict Level of Dynamic Noise of Hydraulic Excavators, by Mikio Iwasaki.
Accuracy of Prediction Methods for Sound Transmission Loss, by K. O. Ballagh.
SITES
http://www.efunda.com/Materials/Alloys/carbon_steels/ show_carbon.cfm?ID=AISI_1020&prop=all&Page_Title=AISI%201020.
http://www.conpargroup.co.uk/evenchan.htm
http://www.engineersedge.com/beam_bending/beam_bending5.htm
http://www.sail.co.in
info@structural-world.org
Notes: <number>

## Slide 47: THANK YOU
Notes: <number>